## DI
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
SUBSTATION-02
RUWAIS - U.A.E.
[10 empty] | FACILITY NAME: BOROUGE 4 |  |  |  | COMPANY PROJ. NO. |  | 4700000897
[14 empty] | CONTRACTOR. PROJ. NO. |  | 083118C
|  | SS-01-HVAC-CP | [7 empty] | DOCUMENT TITLE: SS-02 HVAC PLC System - I/O List |  |  |  | SUBCONTR. ID |  | -
Sl. No. | IM Module | I/O Detail |  |  |  |  | FROM | EQUIPMENT TAG | PLC TAG | Description | States |  | PLC Term. | TB GROUP |  | Verified & Signed (Remarks)
|  | Module | Supply | Type | Range | Unit |  |  |  |  | FALSE | TRUE
DIGITAL INPUT
1 | IM1 | DI1 | 24VDC | VF | - | - | FIELD |  | CHLR1_RUN | CHILLER-1 UNIT RUN STATUS | STOPPED | RUNNING | I0.0 | XDI1-1 | XDI1-2
2 | IM1 | DI1 | 24VDC | VF | - | - | FIELD |  | CHLR1_TRP | CHILLER-1 UNIT TRIP STATUS | NORMAL | TRIP | I0.1 | XDI1-3 | XDI1-4
3 | IM1 | DI1 | 24VDC | VF | - | - | FIELD |  | CHLR1_RMT | CHILLER-1 REMOTE MODE STATUS | LOCAL | REMOTE | I0.2 | XDI1-5 | XDI1-6
4 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-205 |  | CHLR1_BRK_TRP | CHILLER-1 UNIT BREAKER TRIP STATUS | NORMAL | TRIP | I0.3 | XDI1-7 | XDI1-8
5 | IM1 | DI1 | 24VDC | VF | - | - | FIELD |  | CHLR2_RUN | CHILLER-2 UNIT RUN STATUS | STOPPED | RUNNING | I0.4 | XDI1-9 | XDI1-10
6 | IM1 | DI1 | 24VDC | VF | - | - | FIELD |  | CHLR2_TRP | CHILLER-2 UNIT TRIP STATUS | NORMAL | TRIP | I0.5 | XDI1-11 | XDI1-12
7 | IM1 | DI1 | 24VDC | VF | - | - | FIELD |  | CHLR2_RMT | CHILLER-2 REMOTE MODE STATUS | LOCAL | REMOTE | I0.6 | XDI1-13 | XDI1-14
8 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-205 |  | CHLR2_BRK_TRP | CHILLER-2 UNIT BREAKER TRIP STATUS | NORMAL | TRIP | I0.7 | XDI1-15 | XDI1-16
9 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-205 |  | AHU1_RUN | AHU-1 RUN STATUS | STOPPED | RUNNING | I1.4 | XDI1-17 | XDI1-18
10 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-205 |  | AHU1_TRP | AHU-1 TRIP STATUS | NORMAL | TRIP | I1.5 | XDI1-19 | XDI1-20
11 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-205 |  | AHU1_RMT | AHU-1 REMOTE MODE STATUS | LOCAL | REMOTE | I1.6 | XDI1-21 | XDI1-22
12 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-205 |  | AHU1_BRK_TRP | AHU-1 UNIT BREAKER TRIP STATUS | NORMAL | TRIP | I1.7 | XDI1-23 | XDI1-24
13 | IM1 | DI1 | 24VDC | VF | - | - | FIELD |  | AHU1_PF_DPS | AHU-1 PRE-FILTER DIFFERENTIAL PRESSURE HIGH | NORMAL | ALARM | I2.0 | XDI1-25 | XDI1-26
14 | IM1 | DI1 | 24VDC | VF | - | - | FIELD |  | AHU1_FF_DPS | AHU-1 FINE-FILTER DIFFERENTIAL PRESSURE HIGH | NORMAL | ALARM | I2.1 | XDI1-27 | XDI1-28
15 | IM1 | DI1 | 24VDC | VF | - | - | FIELD |  | AHU1_AF_DPS | AHU-1 FAN AIR FLOW DIFFERENTIAL PRESSURE | NO FLOW | FLOW ON | I2.2 | XDI1-29 | XDI1-30
16 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-205 |  | AHU2_RUN | AHU-2 RUN STATUS | STOPPED | RUNNING | I3.1 | XDI1-31 | XDI1-32
17 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-205 |  | AHU2_TRP | AHU-2 TRIP STATUS | NORMAL | TRIP | I3.2 | XDI2-1 | XDI2-2
18 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-205 |  | AHU2_RMT | AHU-2 REMOTE MODE STATUS | LOCAL | REMOTE | I3.3 | XDI2-3 | XDI2-4
19 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-205 |  | AHU2_BRK_TRP | AHU-2 UNIT BREAKER TRIP STATUS | NORMAL | TRIP | I3.4 | XDI2-5 | XDI2-6
20 | IM1 | DI2 | 24VDC | VF | - | - | FIELD |  | AHU2_PF_DPS | AHU-2 PRE-FILTER DIFFERENTIAL PRESSURE HIGH | NORMAL | ALARM | I3.5 | XDI2-7 | XDI2-8
21 | IM1 | DI2 | 24VDC | VF | - | - | FIELD |  | AHU2_FF_DPS | AHU-2 FINE-FILTER DIFFERENTIAL PRESSURE HIGH | NORMAL | ALARM | I3.6 | XDI2-9 | XDI2-10
22 | IM1 | DI2 | 24VDC | VF | - | - | FIELD |  | AHU2_AF_DPS | AHU-2 FAN AIR FLOW DIFFERENTIAL PRESSURE | NO FLOW | FLOW ON | I3.7 | XDI2-11 | XDI2-12
23 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-205 |  | BAT_FAN1_RUN | BATTERY ROOM FAN-1 RUN STATUS | STOPPED | RUNNING | I6.3 | XDI2-13 | XDI2-14
24 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-205 |  | BAT_FAN1_TRP | BATTERY ROOM FAN-1 TRIP STATUS | NORMAL | TRIP | I6.4 | XDI2-15 | XDI2-16
25 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-205 |  | BAT_FAN1_RMT | BATTERY ROOM FAN-1 REMOTE MODE STATUS | LOCAL | REMOTE | I6.5 | XDI2-17 | XDI2-18
26 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-205 |  | BAT_FAN1_ES | BATTERY ROOM FAN-1 EMERGENCY STOP | NORMAL | ACTIVE | I6.6 | XDI2-19 | XDI2-20
27 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-205 |  | BAT_FAN2_RUN | BATTERY ROOM FAN-2 RUN STATUS | STOPPED | RUNNING | I6.7 | XDI2-21 | XDI2-22
28 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-205 |  | BAT_FAN2_TRP | BATTERY ROOM FAN-2 TRIP STATUS | NORMAL | TRIP | I7.0 | XDI2-23 | XDI2-24
29 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-205 |  | BAT_FAN2_RMT | BATTERY ROOM FAN-2 REMOTE MODE STATUS | LOCAL | REMOTE | I7.1 | XDI2-25 | XDI2-26
30 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-205 |  | BAT_FAN2_ES | BATTERY ROOM FAN-2 EMERGENCY STOP | NORMAL | ACTIVE | I7.2 | XDI2-27 | XDI2-28
31 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-205 |  | BLD_FAN_RUN | BLEED FAN RUN STATUS | STOPPED | RUNNING | I6.3 | XDI2-29 | XDI2-30
32 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-205 |  | BLD_FAN_TRP | BLEED FAN TRIP STATUS | NORMAL | TRIP | I6.4 | XDI2-31 | XDI2-32
33 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-205 |  | BLD_FAN_RMT | BLEED FAN REMOTE MODE STATUS | LOCAL | REMOTE | I6.5 | XDI3-1 | XDI3-2
34 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-205 |  | BLD_FAN_ES | BLEED FAN EMERGENCY STOP | NORMAL | ACTIVE | I6.6 | XDI3-3 | XDI3-4
35 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-205 |  | CHLR1_PMP_RUN | CHILLER-1 WATER PUMP RUN STATUS | STOPPED | RUNNING | I6.3 | XDI3-5 | XDI3-6
36 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-205 |  | CHLR1_PMP_TRP | CHILLER-1 WATER PUMP TRIP STATUS | NORMAL | TRIP | I6.4 | XDI3-7 | XDI3-8
37 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-205 |  | CHLR1_PMP_RMT | CHILLER-1 WATER PUMP REMOTE MODE STATUS | LOCAL | REMOTE | I6.5 | XDI3-9 | XDI3-10
38 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-205 |  | CHLR1_PMP_ES | CHILLER-1 WATER PUMP EMERGENCY STOP | NORMAL | ACTIVE | I6.6 | XDI3-11 | XDI3-12
39 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-205 |  | CHLR2_PMP_RUN | CHILLER-2 WATER PUMP RUN STATUS | STOPPED | RUNNING | I6.3 | XDI3-13 | XDI3-14
40 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-205 |  | CHLR2_PMP_TRP | CHILLER-2 WATER PUMP TRIP STATUS | NORMAL | TRIP | I6.4 | XDI3-15 | XDI3-16
41 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-205 |  | CHLR2_PMP_RMT | CHILLER-2 WATER PUMP REMOTE MODE STATUS | LOCAL | REMOTE | I6.5 | XDI3-17 | XDI3-18
42 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-205 |  | CHLR2_PMP_ES | CHILLER-2 WATER PUMP EMERGENCY STOP | NORMAL | ACTIVE | I6.6 | XDI3-19 | XDI3-20
43 | IM1 | DI3 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0205-ZIO | MOTORIZED FIRE DAMPER 141-MFD-0205 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI3-21 | XDI3-22
44 | IM1 | DI3 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0205-ZIC | MOTORIZED FIRE DAMPER 141-MFD-0205 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI3-23 | XDI3-24
45 | IM1 | DI3 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0207-ZIO | MOTORIZED FIRE DAMPER 141-MFD-0207 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI3-25 | XDI3-26
46 | IM1 | DI3 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0207-ZIC | MOTORIZED FIRE DAMPER 141-MFD-0207 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI3-27 | XDI3-28
47 | IM1 | DI3 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0208-ZIO | MOTORIZED FIRE DAMPER 141-MFD-0208 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI3-29 | XDI3-30
48 | IM1 | DI3 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0208-ZIC | MOTORIZED FIRE DAMPER 141-MFD-0208 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI3-31 | XDI3-32
49 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0209-ZIO | MOTORIZED FIRE DAMPER 141-MFD-0209 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI4-1 | XDI4-2
50 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0209-ZIC | MOTORIZED FIRE DAMPER 141-MFD-0209 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI4-3 | XDI4-4
51 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0210-ZIO | MOTORIZED FIRE DAMPER 141-MFD-0210 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI4-5 | XDI4-6
52 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0210-ZIC | MOTORIZED FIRE DAMPER 141-MFD-0210 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI4-7 | XDI4-8
53 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0211-ZIO | MOTORIZED FIRE DAMPER 141-MFD-0211 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI4-9 | XDI4-10
54 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0211-ZIC | MOTORIZED FIRE DAMPER 141-MFD-0211 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI4-11 | XDI4-12
55 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0212-ZIO | MOTORIZED FIRE DAMPER 141-MFD-0212 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI4-13 | XDI4-14
56 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0212-ZIC | MOTORIZED FIRE DAMPER 141-MFD-0212 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI4-15 | XDI4-16
57 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0213-ZIO | MOTORIZED FIRE DAMPER 141-MFD-0213 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI4-17 | XDI4-18
58 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0213-ZIC | MOTORIZED FIRE DAMPER 141-MFD-0213 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI4-19 | XDI4-20
59 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | CHLR1-BFV-ZIO | MOTORIZED BUTTER FLY VALVE CHILLER-1 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI4-21 | XDI4-22
60 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | CHLR1-BFV-ZIC | MOTORIZED BUTTER FLY VALVE CHILLER-1 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI4-23 | XDI4-24
61 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | CHLR2-BFV-ZIO | MOTORIZED BUTTER FLY VALVE CHILLER-2 OPEN STATUS | NOT OPEN | OPEN | I11.6 | XDI4-25 | XDI4-26
62 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | CHLR2-BFV-ZIC | MOTORIZED BUTTER FLY VALVE CHILLER-2 CLOSE STATUS | NOT CLOSE | CLOSE | I11.7 | XDI4-27 | XDI4-28
63 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | BAT_FAN1_DPS | DIFFERENTIAL PRESSURE ACROSS BATTERY ROOM FAN-1 | NO FLOW | FLOW ON | I12.2 | XDI4-29 | XDI4-30
64 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | BAT_FAN2_DPS | DIFFERENTIAL PRESSURE ACROSS BATTERY ROOM FAN-2 | NO FLOW | FLOW ON | I12.2 | XDI4-31 | XDI4-32
65 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | SWG_HTR_TRP | LVSWITCHGEAR ROOM ROOM HEATER TRIP STATUS | NORMAL | TRIP | I12.3 | XDI5-1 | XDI5-2
66 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | RR_HTR_TRP | RACK ROOM HEATER TRIP STATUS | NORMAL | TRIP | I12.4 | XDI5-3 | XDI5-4
67 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | BAT_HTR_TRP | BATTERY ROOM HEATER TRIP STATUS | NORMAL | TRIP | I12.4 | XDI5-5 | XDI5-6
68 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | UPS_HTR_TRP | UPS ROOM HEATER TRIP STATUS | NORMAL | TRIP | I12.2 | XDI5-7 | XDI5-8
69 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | TLR_HTR_TRP | TELECOM ROOM HEATER TRIP STATUS | NORMAL | TRIP | I12.2 | XDI5-9 | XDI5-10
70 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | SWG_HTR_xxx | LVSWITCHGEAR HEATER ON/OFF STATUS | NORMAL | TRIP | I12.2 | XDI5-11 | XDI5-12
71 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | RR_HTR_xxx | RACK ROOM HEATER ON/OFF STATUS | NORMAL | TRIP | I12.2 | XDI5-13 | XDI5-14
72 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | BAT_HTR_xxx | BATTERYROOM HEATER ON/OFF STATUS | NORMAL | TRIP | I12.2 | XDI5-15 | XDI5-16
73 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | UPS_HTR_xxx | UPS ROOM HEATER ON/OFF STATUS | NORMAL | TRIP | I13.1 | XDI5-17 | XDI5-18
74 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | TLR_HTR_xxx | TELECOM HEATER ON/OFF STATUS | NORMAL | TRIP | I13.2 | XDI5-19 | XDI5-20
75 | IM1 | DI5 | 24VDC | VF | - | - | 141-EC-0214 | - | EMG_STP | HVACP EMERGENCY STOP | NORMAL | ACTIVE | I13.4 | XDI5-21 | XDI5-22
76 | IM1 | DI5 | 24VDC | VF | - | - | 141-EC-0214 | - | MUTE_PB | MUTE PUSH BUTTON | OFF | ON | I13.5 | XDI5-23 | XDI5-24
77 | IM1 | DI5 | 24VDC | VF | - | - | 141-EC-0214 | - | RST_PB | RESET PUSH BUTTON | OFF | ON | I13.6 | XDI5-25 | XDI5-26
78 | IM1 | DI5 | 24VDC | VF | - | - | 141-EC-0214 | - | PSU1&2_HLTHY | POWER SUPPLY 1 & 2 HEALTHY | OFF | ON | I13.7 | XDI5-27 | XDI5-28
79 | IM1 | DI5 | 24VDC | VF | - | - | 141-EC-0214 | - | AFS_HLTHY | PANEL AIR FLOW SWITCH HEALTHY | OFF | ON | I14.0 | XDI5-29 | XDI5-30
80 | IM1 | DI5 | 24VDC | VF | - | - | PWR PANEL | - | EMG_MODE | EMERGENCY MODE | EMG MODE OFF | EMG MODE ON | I14.1 | XDI5-31 | XDI5-32
81 | IM1 | DI6 | 24VDC | VF | - | - | LFCP |  | HVAC_SHUT | HVAC SHUTDOWN COMMAND FROM F&G | NORMAL | SHUTDOWN | I14.2 | XDI6-1 | XDI6-2
82 | IM1 | DI6 | 24VDC | VF | - | - | LFCP |  | HVAC_RECR | HVAC RECIRCULATION MODE FROM F&G | NORMAL | RECIRCUL | I14.3 | XDI6-3 | XDI6-4
83 | IM1 | DI6 | 24VDC | VF | - | - | LFCP |  | LFCP_ZONE1 | LFCP ZONE 1 SELECTION | NORMAL | RECIRCUL | I14.4 | XDI6-5 | XDI6-6
84 | IM1 | DI6 | 24VDC | VF | - | - | LFCP | - | LFCP_ZONE2 | LFCP ZONE 2 SELECTION | NOT SELECTED | SELECTED | I14.5 | XDI6-7 | XDI6-8
85 | IM1 | DI6 | 24VDC | VF | - | - | LFCP | - | LFCP_ZONE3 | LFCP ZONE 3 SELECTION | NOT SELECTED | SELECTED | I14.6 | XDI6-9 | XDI6-10
86 | IM1 | DI6 | 24VDC | VF | - | - | LFCP | - | LFCP_ZONE4 | LFCP ZONE 4 SELECTION | NOT SELECTED | SELECTED | I14.7 | XDI6-11 | XDI6-12
87 | IM1 | DI6 | 24VDC | VF | - | - | LFCP | - | LFCP_ZONE5 | LFCP ZONE 5 SELECTION | NOT SELECTED | SELECTED | I15.0 | XDI6-13 | XDI6-14
88 | IM1 | DI6 | 24VDC | VF | - | - | LFCP | - | LFCP_ZONE6 | LFCP ZONE 6 SELECTION | NOT SELECTED | SELECTED | I15.1 | XDI6-15 | XDI6-16
89 | IM1 | DI6 | 24VDC | VF | - | - | LFCP | - | LFCP_ZONE7 | LFCP ZONE 7 SELECTION | NOT SELECTED | SELECTED | I15.2 | XDI6-17 | XDI6-18
90 | IM1 | DI6 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I15.3 | XDI6-19 | XDI6-20
91 | IM1 | DI6 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I15.4 | XDI6-21 | XDI6-22
92 | IM1 | DI6 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I15.5 | XDI6-23 | XDI6-24
93 | IM1 | DI6 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I15.6 | XDI6-25 | XDI6-26
94 | IM1 | DI6 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I15.7 | XDI6-27 | XDI6-28
95 | IM1 | DI6 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I16.0 | XDI6-29 | XDI6-30
96 | IM1 | DI6 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I16.1 | XDI6-31 | XDI6-32
97 | IM1 | DI7 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I14.5 | XDI7-1 | XDI7-2
98 | IM1 | DI7 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I14.6 | XDI7-3 | XDI7-4
99 | IM1 | DI7 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I14.7 | XDI7-5 | XDI7-6
100 | IM1 | DI7 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I15.0 | XDI7-7 | XDI7-8
101 | IM1 | DI7 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I15.1 | XDI7-9 | XDI7-10
102 | IM1 | DI7 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I15.2 | XDI7-11 | XDI7-12
103 | IM1 | DI7 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I15.3 | XDI7-13 | XDI7-14
104 | IM1 | DI7 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I15.4 | XDI7-15 | XDI7-16
105 | IM1 | DI7 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I15.5 | XDI7-17 | XDI7-18
106 | IM1 | DI7 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I15.6 | XDI7-19 | XDI7-20
107 | IM1 | DI7 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I15.7 | XDI7-21 | XDI7-22
108 | IM1 | DI7 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I16.0 | XDI7-23 | XDI7-24
109 | IM1 | DI7 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I16.1 | XDI7-25 | XDI7-26
110 | IM1 | DI7 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I16.2 | XDI7-27 | XDI7-28
111 | IM1 | DI7 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I16.3 | XDI7-29 | XDI7-30
112 | IM1 | DI7 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I16.4 | XDI7-31 | XDI7-32

## DO
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
SUBSTATION-02
RUWAIS - U.A.E.
[10 empty] | FACILITY NAME: BOROUGE 4 |  |  |  | COMPANY PROJ. NO. |  | 4700000897
[14 empty] | CONTRACTOR. PROJ. NO. |  | 083118C
|  | SS-01-HVAC-CP | [7 empty] | DOCUMENT TITLE: SS-02 HVAC PLC System - I/O List |  |  |  | SUBCONTR. ID |  | -
Sl. No. | IM Module | I/O Detail |  |  |  |  | TO | EQUIPMENT TAG | PLC TAG | Description | STATES |  | PLC Term. | TB GROUP |  | Verified & Signed
|  | Module | Supply | Type | Range | Unit |  |  |  |  | FALSE | TRUE
DIGITAL OUTPUT
1 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-205 | 002513006600GB001A | CHLR1_CMD | CHILLER-1 START/STOP COMMAND | STOP | START | Q0.0 | XDO1-1 | XDO1-2
2 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-205 | 002513006600GB001B | CHLR2_CMD | CHILLER-2 START/STOP COMMAND | STOP | START | Q0.1 | XDO1-3 | XDO1-4
3 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-205 | 002513006600GA001A | AHU1_CMD | AHU-1 START/STOP COMMAND | STOP | START | Q0.3 | XDO1-5 | XDO1-6
4 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-205 | 002509006600GA001B | AHU2_CMD | AHU-2 START/STOP COMMAND | STOP | START | Q0.4 | XDO1-7 | XDO1-8
5 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-205 | 002513006600GA006A | BAT_FAN1_CMD | BATTERY ROOM EXHAUST FAN-1 START/STOP COMMAND | STOP | START | Q1.2 | XDO1-9 | XDO1-10
6 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-205 | 002513006600GA006A | BAT_FAN2_CMD | BATTERY ROOM EXHAUST FAN-2 START/STOP COMMAND | STOP | START | Q1.2 | XDO1-11 | XDO1-12
7 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-205 | 002513006600GA006A | CHLR1_BFV_OPN | CHILLER-1 MOTORIZED BUTTER FLY VALVE OPEN COMMAND | NOT OPEN | OPEN | Q1.2 | XDO1-13 | XDO1-14
8 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-205 | 002513006600GA006A | CHLR1_BFV_CLS | CHILLER-1 MOTORIZED BUTTER FLY VALVE CLOSE COMMAND | NOT CLOSE | CLOSE | Q1.2 | XDO1-15 | XDO1-16
9 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-205 | 002513006600GA006A | CHLR2_BFV_OPN | CHILLER-2 MOTORIZED BUTTER FLY VALVE OPEN COMMAND | NOT OPEN | OPEN | Q1.2 | XDO1-17 | XDO1-18
10 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-205 | 002513006600GA006A | CHLR2_BFV_CLS | CHILLER-2 MOTORIZED BUTTER FLY VALVE CLOSE COMMAND | NOT CLOSE | CLOSE | Q1.2 | XDO1-19 | XDO1-20
11 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-205 | 002513006600GA006A | CHLR1_PMP_CMD | CHILLER-1 WATER PUMP START/STOP COMMAND | STOP | START | Q1.2 | XDO1-21 | XDO1-22
12 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-205 | 002513006600GA006A | CHLR2_PMP_CMD | CHILLER-2 WATER PUMP START/STOP COMMAND | STOP | START | Q1.2 | XDO1-23 | XDO1-24
13 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-205 | 002513006600GT001 | SWG_HTR1_CMD | LVSWITCHGEAR ROOM HEATER-1 ON/OFF COMMAND | OFF | ON | Q1.4 | XDO1-25 | XDO1-26
14 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-205 | 002513006600GT002 | RR_HTR_CMD | RACK ROOM HEATER ON/OFF COMMAND | OFF | ON | Q1.5 | XDO1-27 | XDO1-28
15 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-205 | 002513006600GT004 | BAT_HTR_CMD | BATTERY ROOM HEATER ON/OFF COMMAND | OFF | ON | Q1.6 | XDO1-29 | XDO1-30
16 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-205 | 002513006600GT004 | UPS_HTR_CMD | UPS ROOM HEATER ON/OFF COMMAND | OFF | ON | Q1.6 | XDO1-31 | XDO1-32
17 | IM1 | DO2 | 24VDC | VF | - | - | 141-ES-205 | 002513006600GT004 | TLR_HTR_CMD | TELECOM ROOM HEATER ON/OFF COMMAND | OFF | ON | Q1.6 | XDO2-1 | XDO2-2
18 | IM1 | DO2 | 24VDC | 240V | - | - | 141-ES-205 | 141-MFD-0205 | 141-MFD-0205-CMD | MOTORIZED FIRE DAMPER 141-MFD-0205 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-3 | XDO2-4
19 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0207 | 141-MFD-0207-CMD | MOTORIZED FIRE DAMPER 141-MFD-0207 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-5 | XDO2-6
20 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0208 | 141-MFD-0208-CMD | MOTORIZED FIRE DAMPER 141-MFD-0208 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-7 | XDO2-8
21 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0209 | 141-MFD-0209-CMD | MOTORIZED FIRE DAMPER 141-MFD-0209 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-9 | XDO2-10
22 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0210 | 141-MFD-0210-CMD | MOTORIZED FIRE DAMPER 141-MFD-0210 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-11 | XDO2-12
23 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0211 | 141-MFD-0211-CMD | MOTORIZED FIRE DAMPER 141-MFD-0211 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-13 | XDO2-14
24 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0212 | 141-MFD-0212-CMD | MOTORIZED FIRE DAMPER 141-MFD-0212 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-15 | XDO2-16
25 | IM1 | DO2 | 24VDC | VF | - | - | FIELD | 141-MFD-0213 | 141-MFD-0213-CMD | MOTORIZED FIRE DAMPER 141-MFD-0213 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q4.7 | XDO2-17 | XDO2-18
26 | IM1 | DO2 | 24VDC | VF | - | - | PLC | - | BUZZ_ON | BUZZER ON COMMAND | OFF | ON | Q4.7 | XDO2-19 | XDO2-20
27 | IM1 | DO2 | 24VDC | VF | - | - | LFCP | - | HVAC_SHUT_FG | HVAC SHUTDOWN FEEDBACK TO LFCP | OFF | ON | Q5.0 | XDO2-21 | XDO2-22
28 | IM1 | DO2 | 24VDC | VF | - | - | LFCP | - | HVAC_SHUT_FG | RECIRCULATION FEEDBACK TO LFCP | OFF | ON | Q1.7 | XDO2-23 | XDO2-24
29 | IM1 | DO2 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q2.0 | XDO2-25 | XDO2-26
30 | IM1 | DO2 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q2.1 | XDO2-27 | XDO2-28
31 | IM1 | DO2 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q2.2 | XDO2-29 | XDO2-30
32 | IM1 | DO2 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q2.3 | XDO2-31 | XDO2-32
33 | IM1 | DO3 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q2.4 | XDO3-1 | XDO3-2
34 | IM1 | DO3 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q2.5 | XDO3-3 | XDO3-4
35 | IM1 | DO3 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q2.6 | XDO3-5 | XDO3-6
36 | IM1 | DO3 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q2.7 | XDO3-7 | XDO3-8
37 | IM1 | DO3 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q3.0 | XDO3-9 | XDO3-10
38 | IM1 | DO3 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q4.1 | XDO3-11 | XDO3-12
39 | IM1 | DO3 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q4.2 | XDO3-13 | XDO3-14
40 | IM1 | DO3 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q4.3 | XDO3-15 | XDO3-16
41 | IM1 | DO3 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | Q5.1 | XDO3-17 | XDO3-18
42 | IM1 | DO3 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | Q5.2 | XDO3-19 | XDO3-20
43 | IM1 | DO3 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | Q5.3 | XDO3-21 | XDO3-22
44 | IM1 | DO3 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | Q5.4 | XDO3-23 | XDO3-24
45 | IM1 | DO3 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | Q5.5 | XDO3-25 | XDO3-26
46 | IM1 | DO3 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | Q5.6 | XDO3-27 | XDO3-28
47 | IM1 | DO3 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | Q5.7 | XDO3-29 | XDO3-30
48 | IM1 | DO3 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | Q5.7 | XDO3-31 | XDO3-32

## AI
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
SUBSTATION-02
RUWAIS - U.A.E.
[10 empty] | FACILITY NAME: BOROUGE 4 | [5 empty] | COMPANY PROJ. NO. |  | 4700000897
[16 empty] | CONTRACTOR. PROJ. NO. |  | 083118C
| SS-01-HVAC-CP | [8 empty] | DOCUMENT TITLE: SS-02 HVAC PLC System - I/O List | [5 empty] | SUBCONTR. ID |  | -
Sl. No. | IM Module | I/O Detail |  |  |  |  | FROM | EQUIPMENT TAG | PLC TAG | Description | Alarm Setpoints |  |  |  | PLC Term. | TB GROUP |  | Verified & Signed
|  | Module | Supply | Type | Range | Unit |  |  |  |  | LL | L | H | HH
ANALOGUE INPUT
1 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-1 | DPIT-1 | DIFFERENTIAL PRESSURE HVAC ROOM | - | 1 | 5 | - | I0+/I0- | XAI1-1 | XAI1-2
2 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-1 | DPIT-2 | DIFFERENTIAL PRESSURE LV SWT. GR. ROOM | - | 1 | 5 | - | I1+/I1- | XAI1-3 | XAI1-4
3 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-1 | DPIT-3 | DIFFERENTIAL PRESSURE LV SWT. GR. AIRLOCK ROOM | - | 1 | 5 | - | I2+/I2- | XAI1-5 | XAI1-6
4 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-3 | DPIT-5 | DIFFERENTIAL PRESSURE RACK ROOM | - | 1 | 5 | - | I3+/I3- | XAI1-7 | XAI1-8
5 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-3 | DPIT-6 | DIFFERENTIAL PRESSURE RACK AIRLOCK ROOM | - | 1 | 5 | - | I4+/I4- | XAI1-9 | XAI1-10
6 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-3 | DPIT-7 | DIFFERENTIAL PRESSURE TELECOM ROOM | - | 1 | 5 | - | I5+/I5- | XAI1-11 | XAI1-12
7 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-3 | DPIT-8 | DIFFERENTIAL PRESSURE UPS ROOM | - | 1 | 5 | - | I6+/I6- | XAI1-13 | XAI1-14
8 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-2 | DPIT-9 | DIFFERENTIAL PRESSURE BATTERY ROOM | - | 1 | 5 | - | I7+/I7- | XAI1-15 | XAI1-16
9 | IM1 | AI2 | 24VDC | Sink | 0-55 | °C | FIELD | TT-001 | TT-001 | FRESH AIR DUCT TEMPERATURE | - | 20 | 30 | - | I0+/I0- | XAI2-1 | XAI2-2
10 | IM1 | AI2 | 24VDC | Sink | 0-55 | °C | FIELD | TT-002 | TT-002 | RACK ROOM SUPPLY AIR DUCT TEMPERATURE | - | 20 | 30 | - | I1+/I1- | XAI2-3 | XAI2-4
11 | IM1 | AI2 | 24VDC | Sink | 0-55 | °C | FIELD | TT-003 | TT-003 | LV SWT. GR. ROOM SUPPLY AIR DUCT TEMPERATURE | - | 20 | 30 | - | I2+/I2- | XAI2-5 | XAI2-6
12 | IM1 | AI2 | 24VDC | Sink | 0-55 | °C | FIELD | TT-004 | TT-004 | HVAC ROOM TEMPERATURE | - | 20 | 30 | - | I3+/I3- | XAI2-7 | XAI2-8
13 | IM1 | AI2 | 24VDC | Sink | 0-55 | °C | FIELD | TT-005 | TT-005 | LV SWT. GR. ROOM TEMPERATURE | - | 20 | 30 | - | I4+/I4- | XAI2-9 | XAI2-10
14 | IM1 | AI2 | 24VDC | Sink | 0-55 | °C | FIELD | TT-006 | TT-007 | RACK ROOM TEMPERATURE | - | 20 | 30 | - | I5+/I5- | XAI2-11 | XAI2-12
15 | IM1 | AI2 | 24VDC | Sink | 0-55 | °C | FIELD | TT-007 | TT-008 | TELECOM ROOM TEMPERATURE | - | 20 | 30 | - | I6+/I6- | XAI2-13 | XAI2-14
16 | IM1 | AI2 | 24VDC | Sink | 0-55 | °C | 141-ES-205 | TT-008 | TT-009 | UPS ROOM TEMPERATURE | - | 20 | 30 | - | I7+/I7- | XAI2-15 | XAI2-16
17 | IM1 | AI3 | 24VDC | Sink | 0-55 | °C | 141-ES-205 | TT-009 | TT-010 | BATTERY ROOM TEMPERATURE | - | 20 | 30 | - | I0+/I0- | XAI3-1 | XAI3-2
18 | IM1 | AI3 | 24VDC | Sink | 0-100 | °C | 141-ES-205 | HT-001 | HT-001 | RETURN AIR DUCT HUMIDITY | - | 30 | 60 | - | I1+/I1- | XAI3-3 | XAI3-4
19 | IM1 | AI3 | 24VDC | Sink | 0-101 | °C | FIELD | HT-002 | HT-002 | RACK ROOM RETURN AIR DUCT HUMIDITY | - | 30 | 60 | - | I2+/I2- | XAI3-5 | XAI3-6
20 | IM1 | AI3 | 24VDC | Sink | 0-102 | °C | FIELD | HT-003 | HT-003 | LV SWT. GR. ROOM RETURN AIR DUCT HUMIDITY | - | 30 | 60 | - | I3+/I3- | XAI3-7 | XAI3-8
21 | IM1 | AI3 | 24VDC | Sink | 0-103 | °C | FIELD | HT-004 | HT-004 | RACK ROOM SUPPLY AIR DUCT HUMIDITY | - | 30 | 60 | - | I4+/I4- | XAI3-9 | XAI3-10
22 | IM1 | AI3 | 24VDC | Sink | 0-104 | °C | FIELD | HT-005 | HT-005 | LV SWT. GR. ROOM SUPPLY AIR DUCT HUMIDITY | - | 30 | 60 | - | I5+/I5- | XAI3-11 | XAI3-12
23 | IM1 | AI3 | 24VDC | Sink | 0-55 | °C | FIELD | HT-006 | HT-006 | HVAC ROOM HUMIDITY | - | 30 | 60 | - | I6+/I6- | XAI3-13 | XAI3-14
24 | IM1 | AI3 | 24VDC | Sink | 0-55 | °C | FIELD | HT-007 | HT-007 | LV SWT. GR. ROOM HUMIDITY | - | 30 | 60 | - | I7+/I7- | XAI3-15 | XAI3-16
25 | IM1 | AI4 | 24VDC | Sink | 0-55 | °C | FIELD | HT-008 | HT-008 | RACK ROOM HUMIDITY | - | 30 | 60 | - | I0+/I0- | XAI4-1 | XAI4-2
26 | IM1 | AI4 | 24VDC | Sink | 0-55 | °C | FIELD | HT-009 | HT-009 | TELECOM ROOM HUMIDITY | - | 30 | 60 | - | I1+/I1- | XAI4-3 | XAI4-4
27 | IM1 | AI4 | 24VDC | Sink | 0-55 | °C | FIELD | HT-010 | HT-010 | UPS ROOM HUMIDITY | - | 30 | 60 | - | I2+/I2- | XAI4-5 | XAI4-6
28 | IM1 | AI4 | 24VDC | Sink | 0-55 | °C | FIELD | HT-011 | HT-011 | BATTERY ROOM HUMIDITY | - | 30 | 60 | - | I3+/I3- | XAI4-7 | XAI4-8
29 | IM1 | AI4 | 24VDC | Sink | 0-1560 | rpm | FIELD | - | CHLR1-PMP-SPD-FB | CHILLER-1 WATER PUMP SPEED FEEDBACK | - | - | - | - | I4+/I4- | XAI4-9 | XAI4-10
30 | IM1 | AI4 | 24VDC | Sink | 0-100 | % | FIELD | 141-MD-0221 | 141-MD-0221-FB | MODULATING DAMPER MD-0221 POSITION FEEDBACK | - | - | - | - | I5+/I5- | XAI4-11 | XAI4-12
31 | IM1 | AI4 | 24VDC | Sink | 0-100 | % | FIELD | 141-MD-0222 | 141-MD-0222-FB | MODULATING DAMPER MD-0222 POSITION FEEDBACK | - | - | - | - | I6+/I6- | XAI4-13 | XAI4-14
32 | IM1 | AI4 | 24VDC | Sink | 0-100 | % | FIELD | 141-MD-0223 | 141-MD-0223-FB | MODULATING DAMPER MD-0223 POSITION FEEDBACK | - | - | - | - | I7+/I7- | XAI4-15 | XAI4-16
33 | IM1 | AI5 | 24VDC | Sink | 0-100 | % | FIELD | 141-MD-0224 | 141-MD-0224-FB | MODULATING DAMPER MD-0224 POSITION FEEDBACK | - | - | - | - | I0+/I0- | XAI5-1 | XAI5-2
34 | IM1 | AI5 | 24VDC | Sink | 0-100 | % | FIELD | 141-MD-0225 | 141-MD-0225-FB | MODULATING DAMPER MD-0225 POSITION FEEDBACK | - | - | - | - | I1+/I1- | XAI5-3 | XAI5-4
35 | IM1 | AI5 | 24VDC | Sink | 0-100 | % | FIELD | 141-MD-0226 | 141-MD-0226-FB | MODULATING DAMPER MD-0226 POSITION FEEDBACK | - | - | - | - | I2+/I2- | XAI5-5 | XAI5-6
36 | IM1 | AI5 | 24VDC | Sink | 0-100 | % | FIELD | 141-MD-0227 | 141-MD-0227-FB | MODULATING DAMPER MD-0227 POSITION FEEDBACK | - | - | - | - | I3+/I3- | XAI5-7 | XAI5-8
37 | IM1 | AI5 | 24VDC | Sink | - | - | FIELD | - |  | SPARE | - | - | - | - | I4+/I4- | XAI5-9 | XAI5-10
38 | IM1 | AI5 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I5+/I5- | XAI5-11 | XAI5-12
39 | IM1 | AI5 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I6+/I6- | XAI5-13 | XAI5-14
40 | IM1 | AI5 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I7+/I7- | XAI5-15 | XAI5-16

## AO
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
SUBSTATION-02
RUWAIS - U.A.E.
[10 empty] | FACILITY NAME: BOROUGE 4 | [5 empty] | COMPANY PROJ. NO. |  | 4700000897
[16 empty] | CONTRACTOR. PROJ. NO. |  | 083118C
| SS-01-HVAC-CP | [8 empty] | DOCUMENT TITLE: SS-02 HVAC PLC System - I/O List | [5 empty] | SUBCONTR. ID |  | -
Sl. No. | IM Module | I/O Detail |  |  |  |  | TO | EQUIPMENT TAG | PLC TAG | Description | Alarm Setpoints |  |  |  | PLC Term. | TB GROUP |  | Verified & Signed
|  | Module | Supply | Type | Range | Unit |  |  |  |  | LL | L | H | HH
ANALOGUE OUTPUT
1 | IM1 | AO1 | 24VDC | 4-20mA | - | - | CHILLER-1 | 002513006600GB001A | CHLR1_TMP_SP | TEMPERATURE SET POINT TO CHILLER-1 | - | - | - | - | Q0+/Q0- | XAO1-1 | XAO1-2
2 | IM1 | AO1 | 24VDC | 4-20mA | - | - | CHILLER-1 | 002513006600GB001A | CHLR1_RA_TMP | RETURN AIR TEMPETATURE TO CHILLER-1 | - | - | - | - | Q1+/Q1- | XAO1-3 | XAO1-4
3 | IM1 | AO1 | 24VDC | 4-20mA | - | - | CHILLER-2 | 002513006600GB001B | CHLR2_TMP_SP | TEMPERATURE SET POINT TO CHILLER-2 | - | - | - | - | Q2+/Q2- | XAO1-5 | XAO1-6
4 | IM1 | AO1 | 24VDC | 4-20mA | - | - | CHILLER-2 | 002513006600GB001B | CHLR2_RA_TMP | RETURN AIR TEMPETATURE TO CHILLER-2 | - | - | - | - | Q3+/Q3- | XAO1-7 | XAO1-8
5 | IM1 | AO2 | 24VDC | 4-20mA | - | - | - | - | CHLR1-PMP-SPD-REF | CHILLER-1 WATER PUMP SPEED SETPOINT | - | - | - | - | Q2+/Q2- | XAO2-5 | XAO2-6
6 | IM1 | AO2 | 24VDC | 4-20mA | - | - | - | 141-MD-0221 | 141-MD-0221-SP | MODULATING DAMPER MD-0221 SETPOINT | - | - | - | - | Q3+/Q3- | XAO2-7 | XAO2-8
7 | IM1 | AO2 | 24VDC | 4-20mA | - | - | - | 141-MD-0222 | 141-MD-0222-SP | MODULATING DAMPER MD-0222 SETPOINT | - | - | - | - | Q3+/Q3- | XAO2-7 | XAO2-8
8 | IM1 | AO2 | 24VDC | 4-20mA | - | - | - | 141-MD-0223 | 141-MD-0223-SP | MODULATING DAMPER MD-0223 SETPOINT | - | - | - | - | Q3+/Q3- | XAO2-7 | XAO2-8
9 | IM1 | AO3 | 24VDC | 4-20mA | - | - | - | 141-MD-0224 | 141-MD-0224-SP | MODULATING DAMPER MD-0224 SETPOINT | - | - | - | - | Q2+/Q2- | XAO2-5 | XAO2-6
10 | IM1 | AO3 | 24VDC | 4-20mA | - | - | - | 141-MD-0225 | 141-MD-0225-SP | MODULATING DAMPER MD-0225 SETPOINT | - | - | - | - | Q3+/Q3- | XAO2-7 | XAO2-8
11 | IM1 | AO3 | 24VDC | 4-20mA | - | - | - | 141-MD-0226 | 141-MD-0226-SP | MODULATING DAMPER MD-0226 SETPOINT | - | - | - | - | Q3+/Q3- | XAO2-7 | XAO2-8
12 | IM1 | AO3 | 24VDC | 4-20mA | - | - | - | 141-MD-0227 | 141-MD-0227-SP | MODULATING DAMPER MD-0227 SETPOINT | - | - | - | - | Q3+/Q3- | XAO2-7 | XAO2-8
13 | IM1 | AO4 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q2+/Q2- | XAO2-5 | XAO2-6
14 | IM1 | AO4 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q3+/Q3- | XAO2-7 | XAO2-8
15 | IM1 | AO4 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q3+/Q3- | XAO2-7 | XAO2-8
16 | IM1 | AO4 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q3+/Q3- | XAO2-7 | XAO2-8

## IO Summary
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
SUBSTATION-02
RUWAIS - U.A.E.
[8 empty] | FACILITY NAME: BOROUGE 4 | COMPANY PROJ. NO. | 4700000897
[9 empty] | CONTRACTOR. PROJ. NO. | 083118C
SS-01-HVAC-CP | [7 empty] | DOCUMENT TITLE: SS-01 HVAC PLC System - I/O List | SUBCONTR. ID | -
IO SUMMARY
Sl.No | Type | No. Of Channels | No. Of Modules | Count | Used | Spare | Spare %
1 | DI | 16 | 7 | 112 | 89 | 23 | 25.8427
3 | DO | 16 | 3 | 48 | 28 | 20 | 71.4286
4 | AI | 8 | 4 | 32 | 28 | 4 | 14.2857
5 | AO | 4 | 4 | 16 | 12 | 4 | 33.3333

## Sheet1
OPEN STATUS
CLOSE STATUS
MOTORIZED FIRE DAMPER
OPEN/CLOSE COMMAND | 141-MFD-0205 | 141-MFD-0205-ZIO | MOTORIZED FIRE DAMPER 141-MFD-0205 OPEN STATUS | MOTORIZED FIRE DAMPER 141-MFD-0205 OPEN/CLOSE COMMAND | 141-MFD-0205-CMD
| 141-MFD-0205 | 141-MFD-0205-ZIC | MOTORIZED FIRE DAMPER 141-MFD-0205 CLOSE STATUS | MOTORIZED FIRE DAMPER 141-MFD-0207 OPEN/CLOSE COMMAND
| 141-MFD-0207 | 141-MFD-0207-ZIO | MOTORIZED FIRE DAMPER 141-MFD-0207 OPEN STATUS | MOTORIZED FIRE DAMPER 141-MFD-0208 OPEN/CLOSE COMMAND | 141-MFD-0207-CMD
| 141-MFD-0207 | 141-MFD-0207-ZIC | MOTORIZED FIRE DAMPER 141-MFD-0207 CLOSE STATUS | MOTORIZED FIRE DAMPER 141-MFD-0209 OPEN/CLOSE COMMAND
| 141-MFD-0208 | 141-MFD-0208-ZIO | MOTORIZED FIRE DAMPER 141-MFD-0208 OPEN STATUS | MOTORIZED FIRE DAMPER 141-MFD-0210 OPEN/CLOSE COMMAND | 141-MFD-0208-CMD
| 141-MFD-0208 | 141-MFD-0208-ZIC | MOTORIZED FIRE DAMPER 141-MFD-0208 CLOSE STATUS | MOTORIZED FIRE DAMPER 141-MFD-0211 OPEN/CLOSE COMMAND
| 141-MFD-0209 | 141-MFD-0209-ZIO | MOTORIZED FIRE DAMPER 141-MFD-0209 OPEN STATUS | MOTORIZED FIRE DAMPER 141-MFD-0212 OPEN/CLOSE COMMAND | 141-MFD-0209-CMD
| 141-MFD-0209 | 141-MFD-0209-ZIC | MOTORIZED FIRE DAMPER 141-MFD-0209 CLOSE STATUS | MOTORIZED FIRE DAMPER 141-MFD-0213 OPEN/CLOSE COMMAND
| 141-MFD-0210 | 141-MFD-0210-ZIO | MOTORIZED FIRE DAMPER 141-MFD-0210 OPEN STATUS |  | 141-MFD-0210-CMD
| 141-MFD-0210 | 141-MFD-0210-ZIC | MOTORIZED FIRE DAMPER 141-MFD-0210 CLOSE STATUS
| 141-MFD-0211 | 141-MFD-0211-ZIO | MOTORIZED FIRE DAMPER 141-MFD-0211 OPEN STATUS |  | 141-MFD-0211-CMD
| 141-MFD-0211 | 141-MFD-0211-ZIC | MOTORIZED FIRE DAMPER 141-MFD-0211 CLOSE STATUS
| 141-MFD-0212 | 141-MFD-0212-ZIO | MOTORIZED FIRE DAMPER 141-MFD-0212 OPEN STATUS |  | 141-MFD-0212-CMD
| 141-MFD-0212 | 141-MFD-0212-ZIC | MOTORIZED FIRE DAMPER 141-MFD-0212 CLOSE STATUS
| 141-MFD-0213 | 141-MFD-0213-ZIO | MOTORIZED FIRE DAMPER 141-MFD-0213 OPEN STATUS |  | 141-MFD-0213-CMD
| 141-MFD-0213 | 141-MFD-0213-ZIC | MOTORIZED FIRE DAMPER 141-MFD-0213 CLOSE STATUS

## Sheet2
MOTORIZED GAS DAMPER 141-GD-0103 OPEN STATUS
MOTORIZED GAS DAMPER 141-GD-0103 CLOSE STATUS