## DI
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
OPERATING SHELTER
RUWAIS - U.A.E.
[10 empty] | FACILITY NAME: BOROUGE 4 |  |  |  | COMPANY PROJ. NO. |  | 4700000897
[14 empty] | CONTRACTOR. PROJ. NO. |  | 083118C
|  | OS-HVAC-CP | [7 empty] | DOCUMENT TITLE: OS HVAC PLC System - I/O List REV 3 |  |  |  | SUBCONTR. ID |  | -
Sl. No. | IM Module | I/O Detail |  |  |  |  | FROM | EQUIPMENT TAG | PLC TAG | Description | States |  | PLC Term. | TB GROUP |  | Verified & Signed (Remarks)
|  | Module | Supply | Type | Range | Unit |  |  |  |  | FALSE | TRUE
DIGITAL INPUT
1 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 002513006600GB001A | CHLR1_RUN | CHILLER-1 UNIT RUN STATUS | STOPPED | RUNNING | I0.0 | XDI1-1 | XDI1-2
2 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 002513006600GB001A | CHLR1_TRP | CHILLER-1 UNIT TRIP STATUS | NORMAL | TRIP | I0.1 | XDI1-3 | XDI1-4
3 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 002513006600GB001A | CHLR1_RMT | CHILLER-1 REMOTE MODE STATUS | LOCAL | REMOTE | I0.2 | XDI1-5 | XDI1-6
4 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GB001A | CHLR1_BRK_TRP | CHILLER-1 UNIT BREAKER TRIP STATUS | NORMAL | TRIP | I0.3 | XDI1-7 | XDI1-8
5 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 002513006600GB001B | CHLR2_RUN | CHILLER-2 UNIT RUN STATUS | STOPPED | RUNNING | I0.4 | XDI1-9 | XDI1-10
6 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 002513006600GB001B | CHLR2_TRP | CHILLER-2 UNIT TRIP STATUS | NORMAL | TRIP | I0.5 | XDI1-11 | XDI1-12
7 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 002513006600GB001B | CHLR2_RMT | CHILLER-2 REMOTE MODE STATUS | LOCAL | REMOTE | I0.6 | XDI1-13 | XDI1-14
8 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GB001B | CHLR2_BRK_TRP | CHILLER-2 UNIT BREAKER TRIP STATUS | NORMAL | TRIP | I0.7 | XDI1-15 | XDI1-16
9 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA001A | AHU1_RUN | AHU-1 RUN STATUS | STOPPED | RUNNING | I1.4 | XDI1-17 | XDI1-18
10 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA001A | AHU1_TRP | AHU-1 TRIP STATUS | NORMAL | TRIP | I1.5 | XDI1-19 | XDI1-20
11 | IM1 | DI1 | 24VDC | VF | - | - | LCP | 002513006600GA001A | AHU1_RMT | AHU-1 REMOTE MODE STATUS | LOCAL | REMOTE | I1.6 | XDI1-21 | XDI1-22
12 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA001A | AHU1_BRK_TRP | AHU-1 UNIT BREAKER TRIP STATUS | NORMAL | TRIP | I1.7 | XDI1-23 | XDI1-24
13 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 002513006600GA001A | AHU1_PF_DPS | AHU-1 PRE-FILTER DIFFERENTIAL PRESSURE HIGH | NORMAL | ALARM | I2.0 | XDI1-25 | XDI1-26
14 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 002513006600GA001A | AHU1_FF_DPS | AHU-1 FINE-FILTER DIFFERENTIAL PRESSURE HIGH | NORMAL | ALARM | I2.1 | XDI1-27 | XDI1-28
15 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 002513006600GA001A | AHU1_AF_DPS | AHU-1 FAN AIR FLOW DIFFERENTIAL PRESSURE | NO FLOW | FLOW ON | I2.2 | XDI1-29 | XDI1-30
16 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-001 | 002509006600GA001B | AHU2_RUN | AHU-2 RUN STATUS | STOPPED | RUNNING | I3.1 | XDI1-31 | XDI1-32
17 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001 | 002509006600GA001B | AHU2_TRP | AHU-2 TRIP STATUS | NORMAL | TRIP | I3.2 | XDI2-1 | XDI2-2
18 | IM1 | DI2 | 24VDC | VF | - | - | LCP | 002509006600GA001B | AHU2_RMT | AHU-2 REMOTE MODE STATUS | LOCAL | REMOTE | I3.3 | XDI2-3 | XDI2-4
19 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001 | 002509006600GA001B | AHU2_BRK_TRP | AHU-2 UNIT BREAKER TRIP STATUS | NORMAL | TRIP | I3.4 | XDI2-5 | XDI2-6
20 | IM1 | DI2 | 24VDC | VF | - | - | FIELD | 002509006600GA001B | AHU2_PF_DPS | AHU-2 PRE-FILTER DIFFERENTIAL PRESSURE HIGH | NORMAL | ALARM | I3.5 | XDI2-7 | XDI2-8
21 | IM1 | DI2 | 24VDC | VF | - | - | FIELD | 002509006600GA001B | AHU2_FF_DPS | AHU-2 FINE-FILTER DIFFERENTIAL PRESSURE HIGH | NORMAL | ALARM | I3.6 | XDI2-9 | XDI2-10
22 | IM1 | DI2 | 24VDC | VF | - | - | FIELD | 002509006600GA001B | AHU2_AF_DPS | AHU-2 FAN AIR FLOW DIFFERENTIAL PRESSURE | NO FLOW | FLOW ON | I3.7 | XDI2-11 | XDI2-12
23 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006A | BAT_FAN1_RUN | BATTERY ROOM FAN-1 RUN STATUS | STOPPED | RUNNING | I6.3 | XDI2-13 | XDI2-14
24 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006A | BAT_FAN1_TRP | BATTERY ROOM FAN-1 TRIP STATUS | NORMAL | TRIP | I6.4 | XDI2-15 | XDI2-16
25 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006A | BAT_FAN1_RMT | BATTERY ROOM FAN-1 REMOTE MODE STATUS | LOCAL | REMOTE | I6.5 | XDI2-17 | XDI2-18
26 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006A | BAT_FAN1_ES | BATTERY ROOM FAN-1 EMERGENCY STOP | NORMAL | ACTIVE | I6.6 | XDI2-19 | XDI2-20
27 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006B | BAT_FAN2_RUN | BATTERY ROOM FAN-2 RUN STATUS | STOPPED | RUNNING | I6.7 | XDI2-21 | XDI2-22
28 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006B | BAT_FAN2_TRP | BATTERY ROOM FAN-2 TRIP STATUS | NORMAL | TRIP | I7.0 | XDI2-23 | XDI2-24
29 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006B | BAT_FAN2_RMT | BATTERY ROOM FAN-2 REMOTE MODE STATUS | LOCAL | REMOTE | I7.1 | XDI2-25 | XDI2-26
30 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006B | BAT_FAN2_ES | BATTERY ROOM FAN-2 EMERGENCY STOP | NORMAL | ACTIVE | I7.2 | XDI2-27 | XDI2-28
31 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001 |  | BLD_FAN_RUN | BLEED FAN RUN STATUS | STOPPED | RUNNING | I6.3 | XDI2-29 | XDI2-30
32 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001 |  | BLD_FAN_TRP | BLEED FAN TRIP STATUS | NORMAL | TRIP | I6.4 | XDI2-31 | XDI2-32
33 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-001 |  | BLD_FAN_RMT | BLEED FAN REMOTE MODE STATUS | LOCAL | REMOTE | I6.5 | XDI3-1 | XDI3-2
34 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-001 |  | BLD_FAN_ES | BLEED FAN EMERGENCY STOP | NORMAL | ACTIVE | I6.6 | XDI3-3 | XDI3-4
35 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GB001A | CHLR1_PMP_RUN | CHILLER-1 WATER PUMP RUN STATUS | STOPPED | RUNNING | I6.3 | XDI3-5 | XDI3-6
36 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GB001A | CHLR1_PMP_TRP | CHILLER-1 WATER PUMP TRIP STATUS | NORMAL | TRIP | I6.4 | XDI3-7 | XDI3-8
37 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GB001A | CHLR1_PMP_RMT | CHILLER-1 WATER PUMP REMOTE MODE STATUS | LOCAL | REMOTE | I6.5 | XDI3-9 | XDI3-10
38 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GB001A | CHLR1_PMP_ES | CHILLER-1 WATER PUMP EMERGENCY STOP | NORMAL | ACTIVE | I6.6 | XDI3-11 | XDI3-12
39 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GB001B | CHLR2_PMP_RUN | CHILLER-2 WATER PUMP RUN STATUS | STOPPED | RUNNING | I6.3 | XDI3-13 | XDI3-14
40 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GB001B | CHLR2_PMP_TRP | CHILLER-2 WATER PUMP TRIP STATUS | NORMAL | TRIP | I6.4 | XDI3-15 | XDI3-16
41 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GB001B | CHLR2_PMP_RMT | CHILLER-2 WATER PUMP REMOTE MODE STATUS | LOCAL | REMOTE | I6.5 | XDI3-17 | XDI3-18
42 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GB001B | CHLR2_PMP_ES | CHILLER-2 WATER PUMP EMERGENCY STOP | NORMAL | ACTIVE | I6.6 | XDI3-19 | XDI3-20
43 | IM1 | DI3 | 24VDC | VF | - | - | FIELD |  | 141-GD-0301-ZIO | MOTORIZED GAS DAMPER 141-GD-0301 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI3-21 | XDI3-22
44 | IM1 | DI3 | 24VDC | VF | - | - | FIELD |  | 141-GD-0301-ZIC | MOTORIZED GAS DAMPER 141-GD-0301 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI3-23 | XDI3-24
45 | IM1 | DI3 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0302-ZIO | MOTORIZED GAS DAMPER 141-MFD-0302 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI3-25 | XDI3-26
46 | IM1 | DI3 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0302-ZIC | MOTORIZED GAS DAMPER 141-MFD-0302 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI3-27 | XDI3-28
47 | IM1 | DI3 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0303-ZIO | MOTORIZED GAS DAMPER 141-MFD-0303 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI3-29 | XDI3-30
48 | IM1 | DI3 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0303-ZIC | MOTORIZED GAS DAMPER 141-MFD-0303 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI3-31 | XDI3-32
49 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0304-ZIO | MOTORIZED GAS DAMPER 141-MFD-0304 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI4-1 | XDI4-2
50 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0304-ZIC | MOTORIZED GAS DAMPER 141-MFD-0304 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI4-3 | XDI4-4
51 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0305-ZIO | MOTORIZED GAS DAMPER 141-MFD-0305 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI4-5 | XDI4-6
52 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0305-ZIC | MOTORIZED GAS DAMPER 141-MFD-0305 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI4-7 | XDI4-8
53 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0306-ZIO | MOTORIZED GAS DAMPER 141-MFD-0306 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI4-9 | XDI4-10
54 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0306-ZIC | MOTORIZED GAS DAMPER 141-MFD-0306 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI4-11 | XDI4-12
55 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0307-ZIO | MOTORIZED GAS DAMPER 141-MFD-0307 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI4-13 | XDI4-14
56 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0307-ZIC | MOTORIZED GAS DAMPER 141-MFD-0307 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI4-15 | XDI4-16
57 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0308-ZIO | MOTORIZED GAS DAMPER 141-MFD-0308 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI4-17 | XDI4-18
58 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0308-ZIC | MOTORIZED GAS DAMPER 141-MFD-0308 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI4-19 | XDI4-20
59 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0309-ZIO | MOTORIZED GAS DAMPER 141-MFD-0309 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI4-21 | XDI4-22
60 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0309-ZIC | MOTORIZED GAS DAMPER 141-MFD-0309 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI4-23 | XDI4-24
61 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0310-ZIO | MOTORIZED GAS DAMPER 141-MFD-0310 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI4-25 | XDI4-26
62 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0310-ZIC | MOTORIZED GAS DAMPER 141-MFD-0310 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI4-27 | XDI4-28
63 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0311-ZIO | MOTORIZED GAS DAMPER 141-MFD-0311 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI4-29 | XDI4-30
64 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0311-ZIC | MOTORIZED GAS DAMPER 141-MFD-0311 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI4-31 | XDI4-32
65 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0312-ZIO | MOTORIZED GAS DAMPER 141-MFD-0312 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI5-1 | XDI5-2
66 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0312-ZIC | MOTORIZED GAS DAMPER 141-MFD-0312 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI5-3 | XDI5-4
67 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0313-ZIO | MOTORIZED GAS DAMPER 141-MFD-0313 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI5-5 | XDI5-6
68 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0313-ZIC | MOTORIZED GAS DAMPER 141-MFD-0313 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI5-7 | XDI5-8
69 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0314-ZIO | MOTORIZED GAS DAMPER 141-MFD-0314 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI5-9 | XDI5-10
70 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0314-ZIC | MOTORIZED GAS DAMPER 141-MFD-0314 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI5-11 | XDI5-12
71 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0315-ZIO | MOTORIZED GAS DAMPER 141-MFD-0315 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI5-13 | XDI5-14
72 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0315-ZIC | MOTORIZED GAS DAMPER 141-MFD-0315 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI5-15 | XDI5-16
73 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0316-ZIO | MOTORIZED GAS DAMPER 141-MFD-0316 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI5-17 | XDI5-18
74 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0316-ZIC | MOTORIZED GAS DAMPER 141-MFD-0316 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI5-19 | XDI5-20
75 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0317-ZIO | MOTORIZED GAS DAMPER 141-MFD-0317 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI5-21 | XDI5-22
76 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0317-ZIC | MOTORIZED GAS DAMPER 141-MFD-0317 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI5-23 | XDI5-24
77 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0318-ZIO | MOTORIZED GAS DAMPER 141-MFD-0318 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI5-25 | XDI5-26
78 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0318-ZIC | MOTORIZED GAS DAMPER 141-MFD-0318 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI5-27 | XDI5-28
79 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0319-ZIO | MOTORIZED GAS DAMPER 141-MFD-0319 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI5-29 | XDI5-30
80 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0319-ZIC | MOTORIZED GAS DAMPER 141-MFD-0319 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI5-31 | XDI5-32
81 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0320-ZIO | MOTORIZED GAS DAMPER 141-MFD-0320 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI6-1 | XDI6-2
82 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0320-ZIC | MOTORIZED GAS DAMPER 141-MFD-0320 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI6-3 | XDI6-4
83 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0321-ZIO | MOTORIZED GAS DAMPER 141-MFD-0321 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI6-5 | XDI6-6
84 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0321-ZIC | MOTORIZED GAS DAMPER 141-MFD-0321 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI6-7 | XDI6-8
85 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0322-ZIO | MOTORIZED GAS DAMPER 141-MFD-0322 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI6-9 | XDI6-10
86 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0322-ZIC | MOTORIZED GAS DAMPER 141-MFD-0322 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI6-11 | XDI6-12
87 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0323-ZIO | MOTORIZED GAS DAMPER 141-MFD-0323 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI6-13 | XDI6-14
88 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0323-ZIC | MOTORIZED GAS DAMPER 141-MFD-0323 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI6-15 | XDI6-16
89 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0324-ZIO | MOTORIZED GAS DAMPER 141-MFD-0324 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI6-17 | XDI6-18
90 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0324-ZIC | MOTORIZED GAS DAMPER 141-MFD-0324 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI6-19 | XDI6-20
91 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0325-ZIO | MOTORIZED GAS DAMPER 141-MFD-0325 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI6-21 | XDI6-22
92 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0325-ZIC | MOTORIZED GAS DAMPER 141-MFD-0325 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI6-23 | XDI6-24
93 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0326-ZIO | MOTORIZED GAS DAMPER 141-MFD-0326 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI6-25 | XDI6-26
94 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0326-ZIC | MOTORIZED GAS DAMPER 141-MFD-0326 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI6-27 | XDI6-28
95 | IM1 | DI6 | 24VDC | VF | - | - | FIELD | 002513006600GB001A | CHLR1-BFV-ZIO | MOTORIZED BUTTER FLY VALVE CHILLER-1 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI6-29 | XDI6-30
96 | IM1 | DI6 | 24VDC | VF | - | - | FIELD | 002513006600GB001A | CHLR1-BFV-ZIC | MOTORIZED BUTTER FLY VALVE CHILLER-1 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI6-31 | XDI6-32
97 | IM1 | DI7 | 24VDC | VF | - | - | FIELD | 002513006600GB001B | CHLR2-BFV-ZIO | MOTORIZED BUTTER FLY VALVE CHILLER-2 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI7-1 | XDI7-2
98 | IM1 | DI7 | 24VDC | VF | - | - | FIELD | 002513006600GB001B | CHLR2-BFV-ZIC | MOTORIZED BUTTER FLY VALVE CHILLER-2 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI7-3 | XDI7-4
99 | IM1 | DI7 | 24VDC | VF | - | - | FIELD | 002513006600GA006A | BAT_FAN1_DPS | DIFFERENTIAL PRESSURE ACROSS BATTERY ROOM FAN-1 | NO FLOW | FLOW ON | I9.6 | XDI7-5 | XDI7-6
100 | IM1 | DI7 | 24VDC | VF | - | - | FIELD | 002513006600GA006B | BAT_FAN2_DPS | DIFFERENTIAL PRESSURE ACROSS BATTERY ROOM FAN-2 | NO FLOW | FLOW ON | I9.7 | XDI7-7 | XDI7-8
101 | IM1 | DI7 | 24VDC | VF | - | - | FIELD |  | MW_HTR_TRP | MACHINE WORKSHOP HEATER TRIP STATUS | NORMAL | TRIP | I9.6 | XDI7-9 | XDI7-10
102 | IM1 | DI7 | 24VDC | VF | - | - | FIELD |  | EIW_HTR_TRP | E&I WORKSHOP HEATER TRIP STATUS | NORMAL | TRIP | I9.7 | XDI7-11 | XDI7-12
103 | IM1 | DI7 | 24VDC | VF | - | - | FIELD |  | MTO_HTR_TRP | MAINTENANCE TECHNICIAN OFFICE HEATER TRIP STATUS | NORMAL | TRIP | I11.6 | XDI7-13 | XDI7-14
104 | IM1 | DI7 | 24VDC | VF | - | - | FIELD |  | TLR_HTR_TRP | TELECOM ROOM HEATER TRIP STATUS | NORMAL | TRIP | I11.7 | XDI7-15 | XDI7-16
105 | IM1 | DI7 | 24VDC | VF | - | - | FIELD |  | MSU_HTR_TRP | MAINTENANCE SUPERVISOR OFFICE HEATER TRIP STATUS | NORMAL | TRIP | I12.2 | XDI7-17 | XDI7-18
106 | IM1 | DI7 | 24VDC | VF | - | - | FIELD |  | EUO_HTR_TRP | EU OPERATORS OFFICE HEATER TRIP STATUS | NORMAL | TRIP | I12.2 | XDI7-19 | XDI7-20
107 | IM1 | DI7 | 24VDC | VF | - | - | FIELD |  | TR_HTR_TRP | TEA ROOM HEATER TRIP STATUS | NORMAL | TRIP | I12.2 | XDI7-21 | XDI7-22
108 | IM1 | DI7 | 24VDC | VF | - | - | FIELD |  | MW_HTR_xxx | MACHINE WORKSHOP HEATER ON/OFF STATUS | NORMAL | TRIP | I12.2 | XDI7-23 | XDI7-24
109 | IM1 | DI7 | 24VDC | VF | - | - | FIELD |  | EIW_HTR_xxx | E&I WORKSHOP HEATER ON/OFF STATUS | NORMAL | TRIP | I12.3 | XDI7-25 | XDI7-26
110 | IM1 | DI7 | 24VDC | VF | - | - | FIELD |  | MTO_HTR_xxx | MAINTENANCE TECHNICIAN OFFICE HEATER ON/OFF STATUS | NORMAL | TRIP | I12.4 | XDI7-27 | XDI7-28
111 | IM1 | DI7 | 24VDC | VF | - | - | FIELD |  | TLR_HTR_xxx | TELECOM ROOM HEATER ON/OFF STATUS | NORMAL | TRIP | I12.4 | XDI7-29 | XDI7-30
112 | IM1 | DI7 | 24VDC | VF | - | - | FIELD |  | MSU_HTR_xxx | MAINTENANCE SUPERVISOR OFFICE HEATER ON/OFF STATUS | NORMAL | TRIP | I12.2 | XDI7-31 | XDI7-32
113 | IM1 | DI8 | 24VDC | VF | - | - | FIELD |  | EUO_HTR_xxx | EU OPERATORS OFFICE HEATER ON/OFF STATUS | NORMAL | TRIP | I12.2 | XDI8-1 | XDI8-2
114 | IM1 | DI8 | 24VDC | VF | - | - | FIELD |  | TR_HTR_xxx | TEA ROOM HEATER ON/OFF STATUS | NORMAL | TRIP | I12.2 | XDI8-3 | XDI8-4
115 | IM1 | DI8 | 24VDC | VF | - | - | 141-EC-0001 | - | EMG_STP | HVACP EMERGENCY STOP | NORMAL | ACTIVE | I12.2 | XDI8-5 | XDI8-6
116 | IM1 | DI8 | 24VDC | VF | - | - | 141-EC-0001 | - | MUTE_PB | MUTE PUSH BUTTON | OFF | ON | I12.2 | XDI8-7 | XDI8-8
117 | IM1 | DI8 | 24VDC | VF | - | - | 141-EC-0001 | - | RST_PB | RESET PUSH BUTTON | OFF | ON | I12.2 | XDI8-9 | XDI8-10
118 | IM1 | DI8 | 24VDC | VF | - | - | 141-EC-0001 | - | PSU1&2_HLTHY | POWER SUPPLY 1 & 2 HEALTHY | UNHEALTHY | HEALTHY | I12.2 | XDI8-11 | XDI8-12
119 | IM1 | DI8 | 24VDC | VF | - | - | 141-EC-0001 | - | AFS_HLTHY | PANEL AIR FLOW SWITCH HEALTHY | UNHEALTHY | HEALTHY | I13.1 | XDI8-13 | XDI8-14
120 | IM1 | DI8 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I13.2 | XDI8-15 | XDI8-16
121 | IM1 | DI8 | 24VDC | VF | - | - | LFCP |  | HVAC_SHUT | HVAC SHUTDOWN COMMAND FROM F&G AND ALL DAMPERS CLOSE | NORMAL | SHUTDOWN | I13.4 | XDI8-17 | XDI8-18
122 | IM1 | DI8 | 24VDC | VF | - | - | LFCP |  | HVAC_RECR | HVAC RECIRCULATION MODE FROM F&G AIR INTAKE DAMPER CLOSE | NORMAL | RECIRCUL | I13.5 | XDI8-19 | XDI8-20
123 | IM1 | DI8 | 24VDC | VF | - | - | LFCP |  | LFCP_ZONE1 | LFCP ZONE 1 SELECTION | NOT SELECTED | SELECTED | I13.6 | XDI8-21 | XDI8-22
124 | IM1 | DI8 | 24VDC | VF | - | - | LFCP | - | LFCP_ZONE2 | LFCP ZONE 2 SELECTION | NOT SELECTED | SELECTED | I13.7 | XDI8-23 | XDI8-24
125 | IM1 | DI8 | 24VDC | VF | - | - | LFCP | - | LFCP_ZONE3 | LFCP ZONE 3 SELECTION | NOT SELECTED | SELECTED | I14.0 | XDI8-25 | XDI8-26
126 | IM1 | DI8 | 24VDC | VF | - | - | LFCP | - | LFCP_ZONE4 | LFCP ZONE 4 SELECTION | NOT SELECTED | SELECTED | I14.1 | XDI8-27 | XDI8-28
127 | IM1 | DI8 | 24VDC | VF | - | - | LFCP | - | LFCP_ZONE5 | LFCP ZONE 5 SELECTION | NOT SELECTED | SELECTED | I14.2 | XDI8-29 | XDI8-30
128 | IM1 | DI8 | 24VDC | VF | - | - | LFCP | - | LFCP_ZONE6 | LFCP ZONE 6 SELECTION | NOT SELECTED | SELECTED | I14.3 | XDI8-31 | XDI8-32
129 | IM1 | DI9 | 24VDC | VF | - | - | LFCP | - | LFCP_ZONE7 | LFCP ZONE 7 SELECTION | NOT SELECTED | SELECTED | I14.4 | XDI9-1 | XDI9-2
130 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I14.5 | XDI9-3 | XDI9-4
131 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I14.6 | XDI9-5 | XDI9-6
132 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I14.7 | XDI9-7 | XDI9-8
133 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I15.0 | XDI9-9 | XDI9-10
134 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I15.1 | XDI9-11 | XDI9-12
135 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I15.2 | XDI9-13 | XDI9-14
136 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I15.3 | XDI9-15 | XDI9-16
137 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I15.4 | XDI9-17 | XDI9-18
138 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I15.5 | XDI9-19 | XDI9-20
139 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I15.6 | XDI9-21 | XDI9-22
140 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I15.7 | XDI9-23 | XDI9-24
141 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I16.0 | XDI9-25 | XDI9-26
142 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I16.1 | XDI9-27 | XDI9-28
143 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I16.2 | XDI9-29 | XDI9-30
144 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I16.3 | XDI9-31 | XDI9-32
145 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I16.4 | XDI10-1 | XDI10-2
146 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I16.5 | XDI10-3 | XDI10-4
147 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I16.6 | XDI10-5 | XDI10-6
148 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I16.7 | XDI10-7 | XDI10-8
149 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.0 | XDI10-9 | XDI10-10
150 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.1 | XDI10-11 | XDI10-12
151 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.2 | XDI10-13 | XDI10-14
152 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.3 | XDI10-15 | XDI10-16
153 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.4 | XDI10-17 | XDI10-18
154 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.5 | XDI10-19 | XDI10-20
155 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.6 | XDI10-21 | XDI10-22
156 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.7 | XDI10-23 | XDI10-24
157 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.2 | XDI10-25 | XDI10-26
158 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.3 | XDI10-27 | XDI10-28
159 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.4 | XDI10-29 | XDI10-30
160 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.5 | XDI10-31 | XDI10-32

## DO
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
OPERATING SHELTER
RUWAIS - U.A.E.
[10 empty] | FACILITY NAME: BOROUGE 4 |  |  |  | COMPANY PROJ. NO. |  | 4700000897
[14 empty] | CONTRACTOR. PROJ. NO. |  | 083118C
|  | OS-HVAC-CP | [7 empty] | DOCUMENT TITLE: OS HVAC PLC System - I/O List REV 3 |  |  |  | SUBCONTR. ID |  | -
Sl. No. | IM Module | I/O Detail |  |  |  |  | TO | EQUIPMENT TAG | PLC TAG | Description | STATES |  | PLC Term. | TB GROUP |  | Verified & Signed
|  | Module | Supply | Type | Range | Unit |  |  |  |  | FALSE | TRUE
DIGITAL OUTPUT
1 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GB001A | CHLR1_CMD | CHILLER-1 START/STOP COMMAND | STOP | START | Q0.0 | XDO1-1 | XDO1-2
2 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GB001B | CHLR2_CMD | CHILLER-2 START/STOP COMMAND | STOP | START | Q0.1 | XDO1-3 | XDO1-4
3 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA001A | AHU1_CMD | AHU-1 START/STOP COMMAND | STOP | START | Q0.3 | XDO1-5 | XDO1-6
4 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002509006600GA001B | AHU2_CMD | AHU-2 START/STOP COMMAND | STOP | START | Q0.4 | XDO1-7 | XDO1-8
5 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006A | BAT_FAN1_CMD | BATTERY ROOM EXHAUST FAN-1 START/STOP COMMAND | STOP | START | Q1.2 | XDO1-9 | XDO1-10
6 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006A | BAT_FAN2_CMD | BATTERY ROOM EXHAUST FAN-2 START/STOP COMMAND | STOP | START | Q1.2 | XDO1-11 | XDO1-12
7 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006A | CHLR1_BFV_OPN | CHILLER-1 MOTORIZED BUTTER FLY VALVE OPEN COMMAND | NOT OPEN | OPEN | Q1.2 | XDO1-13 | XDO1-14
8 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006A | CHLR1_BFV_CLS | CHILLER-1 MOTORIZED BUTTER FLY VALVE CLOSE COMMAND | NOT CLOSE | CLOSE | Q1.2 | XDO1-15 | XDO1-16
9 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006A | CHLR2_BFV_OPN | CHILLER-2 MOTORIZED BUTTER FLY VALVE OPEN COMMAND | NOT OPEN | OPEN | Q1.2 | XDO1-17 | XDO1-18
10 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006A | CHLR2_BFV_CLS | CHILLER-2 MOTORIZED BUTTER FLY VALVE CLOSE COMMAND | NOT CLOSE | CLOSE | Q1.2 | XDO1-19 | XDO1-20
11 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006A | CHLR1_PMP_CMD | CHILLER-1 WATER PUMP START/STOP COMMAND | STOP | START | Q1.2 | XDO1-21 | XDO1-22
12 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006A | CHLR2_PMP_CMD | CHILLER-2 WATER PUMP START/STOP COMMAND | STOP | START | Q1.2 | XDO1-23 | XDO1-24
13 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GT001 | MW_HTR_CMD | MACHINE WORKSHOP HEATER ON/OFF COMMAND | OFF | ON | Q1.4 | XDO1-25 | XDO1-26
14 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GT001 | EIW_HTR_CMD | E&I WORKSHOP HEATER ON/OFF COMMAND | OFF | ON | Q1.4 | XDO1-27 | XDO1-28
15 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GT001 | MTO_HTR_CMD | MAINTENANCE TECHNICIAN OFFICE HEATER ON/OFF COMMAND | OFF | ON | Q1.4 | XDO1-29 | XDO1-30
16 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GT002 | TLR_HTR_CMD | TELECOM ROOM HEATER ON/OFF COMMAND | OFF | ON | Q1.5 | XDO1-31 | XDO1-32
17 | IM1 | DO2 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GT001 | MSU_HTR_CMD | MAINTENANCE SUPERVISOR OFFICE HEATER ON/OFF COMMAND | OFF | ON | Q1.4 | XDO2-1 | XDO2-2
18 | IM1 | DO2 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GT001 | EUO_HTR_CMD | EU OPERATORS OFFICE HEATER ON/OFF COMMAND | OFF | ON | Q1.4 | XDO2-3 | XDO2-4
19 | IM1 | DO2 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GT001 | TR_HTR_CMD | TEA ROOM HEATER ON/OFF COMMAND | OFF | ON | Q1.4 | XDO2-5 | XDO2-6
20 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-GD-0301 | 141-GD-0301-CMD | MOTORIZED GAS DAMPER 141-GD-0301 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-7 | XDO2-8
21 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0302 | 141-MFD-0302-CMD | MOTORIZED FIRE DAMPER 141-MFD-0302 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-9 | XDO2-10
22 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0303 | 141-MFD-0303-CMD | MOTORIZED FIRE DAMPER 141-MFD-0303 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-11 | XDO2-12
23 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0304 | 141-MFD-0304-CMD | MOTORIZED FIRE DAMPER 141-MFD-0304 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-13 | XDO2-14
24 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0305 | 141-MFD-0305-CMD | MOTORIZED FIRE DAMPER 141-MFD-0305 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-15 | XDO2-16
25 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0306 | 141-MFD-0306-CMD | MOTORIZED FIRE DAMPER 141-MFD-0306 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-17 | XDO2-18
26 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0307 | 141-MFD-0307-CMD | MOTORIZED FIRE DAMPER 141-MFD-0307 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-19 | XDO2-20
27 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0308 | 141-MFD-0308-CMD | MOTORIZED FIRE DAMPER 141-MFD-0308 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-21 | XDO2-22
28 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0309 | 141-MFD-0309-CMD | MOTORIZED FIRE DAMPER 141-MFD-0309 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-23 | XDO2-24
29 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0310 | 141-MFD-0310-CMD | MOTORIZED FIRE DAMPER 141-MFD-0310 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-25 | XDO2-26
30 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0311 | 141-MFD-0311-CMD | MOTORIZED FIRE DAMPER 141-MFD-0311 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-27 | XDO2-28
31 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0312 | 141-MFD-0312-CMD | MOTORIZED FIRE DAMPER 141-MFD-0312 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-29 | XDO2-30
32 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0313 | 141-MFD-0313-CMD | MOTORIZED FIRE DAMPER 141-MFD-0313 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-31 | XDO2-32
33 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-MFD-0314 | 141-MFD-0314-CMD | MOTORIZED FIRE DAMPER 141-MFD-0314 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-1 | XDO3-2
34 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-MFD-0315 | 141-MFD-0315-CMD | MOTORIZED FIRE DAMPER 141-MFD-0315 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-3 | XDO3-4
35 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-MFD-0316 | 141-MFD-0316-CMD | MOTORIZED FIRE DAMPER 141-MFD-0316 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-5 | XDO3-6
36 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-MFD-0317 | 141-MFD-0317-CMD | MOTORIZED FIRE DAMPER 141-MFD-0317 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-7 | XDO3-8
37 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-MFD-0318 | 141-MFD-0318-CMD | MOTORIZED FIRE DAMPER 141-MFD-0318 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-9 | XDO3-10
38 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-MFD-0319 | 141-MFD-0319-CMD | MOTORIZED FIRE DAMPER 141-MFD-0319 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-11 | XDO3-12
39 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-MFD-0320 | 141-MFD-0320-CMD | MOTORIZED FIRE DAMPER 141-MFD-0320 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-13 | XDO3-14
40 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-MFD-0321 | 141-MFD-0321-CMD | MOTORIZED FIRE DAMPER 141-MFD-0321 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-15 | XDO3-16
41 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-MFD-0322 | 141-MFD-0322-CMD | MOTORIZED FIRE DAMPER 141-MFD-0322 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-17 | XDO3-18
42 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-MFD-0323 | 141-MFD-0323-CMD | MOTORIZED FIRE DAMPER 141-MFD-0323 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-19 | XDO3-20
43 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-MFD-0324 | 141-MFD-0324-CMD | MOTORIZED FIRE DAMPER 141-MFD-0324 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-21 | XDO3-22
44 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-MFD-0325 | 141-MFD-0325-CMD | MOTORIZED FIRE DAMPER 141-MFD-0325 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-23 | XDO3-24
45 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-MFD-0326 | 141-MFD-0326-CMD | MOTORIZED FIRE DAMPER 141-MFD-0326 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-25 | XDO3-26
46 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-GD-0137 | 141-GD-0334-CMD | MOTORIZED GAS DAMPER 141-GD-0334 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-27 | XDO3-28
47 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-GD-0137 | 141-GD-0336-CMD | MOTORIZED GAS DAMPER 141-GD-0336 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-29 | XDO3-30
48 | IM1 | DO3 | 24VDC | VF | - | - | F&G | - | HVAC_SHUT_FG | HVAC SHUTDOWN/DAMPER CLOSE FEEDBACK TO F&G | OFF | ON | Q4.7 | XDO3-31 | XDO3-32
49 | IM1 | DO4 | 24VDC | VF | - | - | F&G | - | HVAC_SHUT_FG | RECIRCULATION/DAMPER CLOSE FEEDBACK TO F&G | OFF | ON | Q4.7 | XDO4-1 | XDO4-2
50 | IM1 | DO4 | 24VDC | VF | - | - | PLC | - | BUZZ_ON | BUZZER ON COMMAND | OFF | ON | Q5.0 | XDO4-3 | XDO4-4
51 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE |  |  | Q4.1 | XDO4-5 | XDO4-6
52 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE |  |  | Q4.2 | XDO4-7 | XDO4-8
53 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE |  |  | Q4.3 | XDO4-9 | XDO4-10
54 | IM1 | DO4 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | Q1.7 | XDO4-11 | XDO4-12
55 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE |  |  | Q2.0 | XDO4-13 | XDO4-14
56 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE |  |  | Q2.1 | XDO4-15 | XDO4-16
57 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE |  |  | Q2.2 | XDO4-17 | XDO4-18
58 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE |  |  | Q2.3 | XDO4-19 | XDO4-20
59 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE |  |  | Q2.4 | XDO4-21 | XDO4-22
60 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE |  |  | Q2.5 | XDO4-23 | XDO4-24
61 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE |  |  | Q2.6 | XDO4-25 | XDO4-26
62 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE |  |  | Q2.7 | XDO4-27 | XDO4-28
63 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE |  |  | Q3.0 | XDO4-29 | XDO4-30
64 | IM1 | DO4 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | Q5.1 | XDO4-31 | XDO4-32

## AI
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
OPERATING SHELTER
RUWAIS - U.A.E.
[10 empty] | FACILITY NAME: BOROUGE 4 | [5 empty] | COMPANY PROJ. NO. |  | 4700000897
[16 empty] | CONTRACTOR. PROJ. NO. |  | 083118C
| OS-HVAC-CP | [8 empty] | DOCUMENT TITLE: OS HVAC PLC System - I/O List REV 3 | [5 empty] | SUBCONTR. ID |  | -
Sl. No. | IM Module | I/O Detail |  |  |  |  | FROM | EQUIPMENT TAG | PLC TAG | Description | Alarm Setpoints |  |  |  | PLC Term. | TB GROUP |  | Verified & Signed
|  | Module | Supply | Type | Range | Unit |  |  |  |  | LL | L | H | HH
ANALOGUE INPUT
1 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-1 | DPIT-1 | DIFFERENTIAL PRESSURE HVAC ROOM | - | 1 | 5 | - | I0+/I0- | XAI1-1 | XAI1-2
2 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-2 | DPIT-2 | DIFFERENTIAL PRESSURE EQUIPMENT TOOL ROOM | - | 1 | 5 | - | I1+/I1- | XAI1-3 | XAI1-4
3 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-3 | DPIT-3 | DIFFERENTIAL PRESSURE MACHINE WORKSHOP | - | 1 | 5 | - | I2+/I2- | XAI1-5 | XAI1-6
4 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-4 | DPIT-4 | DIFFERENTIAL PRESSURE E&I WORKSHOP | - | 1 | 5 | - | I3+/I3- | XAI1-7 | XAI1-8
5 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-5 | DPIT-5 | DIFFERENTIAL PRESSURE E&I WORKSHOP AIRLOCK | - | 1 | 5 | - | I4+/I4- | XAI1-9 | XAI1-10
6 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-6 | DPIT-6 | DIFFERENTIAL PRESSURE CONSUMABLE STORE | - | 1 | 5 | - | I5+/I5- | XAI1-11 | XAI1-12
7 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-7 | DPIT-7 | DIFFERENTIAL PRESSURE EU OPERATORS OFFICE | - | 1 | 5 | - | I6+/I6- | XAI1-13 | XAI1-14
8 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-8 | DPIT-8 | DIFFERENTIAL PRESSURE MAINTENANCE SUPERVISOR OFFICE | - | 1 | 5 | - | I7+/I7- | XAI1-15 | XAI1-16
9 | IM1 | AI2 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-9 | DPIT-9 | DIFFERENTIAL PRESSURE TELECOM F&G ROOM | - | 1 | 5 | - | I0+/I0- | XAI2-1 | XAI2-2
10 | IM1 | AI2 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-10 | DPIT-10 | DIFFERENTIAL PRESSURE TELECOM F&G ROOM AIRLOCK | - | 1 | 5 | - | I1+/I1- | XAI2-3 | XAI2-4
11 | IM1 | AI2 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-11 | DPIT-11 | DIFFERENTIAL PRESSURE MAINTENACE TECHNICIAN OFFICE | - | 1 | 5 | - | I2+/I2- | XAI2-5 | XAI2-6
12 | IM1 | AI2 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-12 | DPIT-12 | DIFFERENTIAL PRESSURE TEA ROOM | - | 1 | 5 | - | I3+/I3- | XAI2-7 | XAI2-8
13 | IM1 | AI2 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-13 | DPIT-13 | DIFFERENTIAL PRESSURE TOILET | - | 1 | 5 | - | I4+/I4- | XAI2-9 | XAI2-10
14 | IM1 | AI2 | 24VDC | Sink | 0-55 | °C | FIELD | TT-001 | TT-001 | FRESH AIR DUCT TEMPERATURE | - | 20 | 30 | - | I5+/I5- | XAI2-11 | XAI2-12
15 | IM1 | AI2 | 24VDC | Sink | 0-55 | °C | FIELD | TT-002 | TT-002 | SUPPLY AIR DUCT TEMPERATURE | - | 20 | 30 | - | I6+/I6- | XAI2-13 | XAI2-14
16 | IM1 | AI2 | 24VDC | Sink | 0-55 | °C | FIELD | TT-003 | TT-003 | HVAC ROOM TEMPERATURE | - | 20 | 30 | - | I7+/I7- | XAI2-15 | XAI2-16
17 | IM1 | AI3 | 24VDC | Sink | 0-55 | °C | FIELD | TT-004 | TT-004 | EQUIPMENT TOOL ROOM TEMPERATURE | - | 20 | 30 | - | I0+/I0- | XAI3-1 | XAI3-2
18 | IM1 | AI3 | 24VDC | Sink | 0-55 | °C | FIELD | TT-005 | TT-005 | MACHINE WORKSHOP TEMPERATURE | - | 20 | 30 | - | I1+/I1- | XAI3-3 | XAI3-4
19 | IM1 | AI3 | 24VDC | Sink | 0-55 | °C | FIELD | TT-006 | TT-006 | E&I WORKSHOP TEMPERATURE | - | 20 | 30 | - | I2+/I2- | XAI3-5 | XAI3-6
20 | IM1 | AI3 | 24VDC | Sink | 0-55 | °C | FIELD | TT-007 | TT-007 | CONSUMABLE STORE TEMPERATURE | - | 20 | 30 | - | I3+/I3- | XAI3-7 | XAI3-8
21 | IM1 | AI3 | 24VDC | Sink | 0-55 | °C | FIELD | TT-008 | TT-008 | EU OPERATORS OFFICE TEMPERATURE | - | 20 | 30 | - | I4+/I4- | XAI3-9 | XAI3-10
22 | IM1 | AI3 | 24VDC | Sink | 0-55 | °C | FIELD | TT-009 | TT-009 | MAINTENANCE SUPERVISOR OFFICE TEMPERATURE | - | 20 | 30 | - | I5+/I5- | XAI3-11 | XAI3-12
23 | IM1 | AI3 | 24VDC | Sink | 0-55 | °C | FIELD | TT-010 | TT-010 | TELECOM F&G ROOM TEMPERATURE | - | 20 | 30 | - | I6+/I6- | XAI3-13 | XAI3-14
24 | IM1 | AI3 | 24VDC | Sink | 0-55 | °C | FIELD | TT-011 | TT-011 | MAINTENACE TECHNICIAN OFFICE TEMPERATURE | - | 20 | 30 | - | I7+/I7- | XAI3-15 | XAI3-16
25 | IM1 | AI4 | 24VDC | Sink | 0-55 | °C | FIELD | TT-012 | TT-012 | TEA ROOM TEMPERATURE | - | 20 | 30 | - | I0+/I0- | XAI4-1 | XAI4-2
26 | IM1 | AI4 | 24VDC | Sink | 0-55 | °C | FIELD | TT-013 | TT-013 | TOILET TEMPERATURE | - | 20 | 30 | - | I1+/I1- | XAI4-3 | XAI4-4
27 | IM1 | AI4 | 24VDC | Sink | 0-100 | °C | FIELD | HT-001 | HT-001 | SUPPLY AIR DUCT HUMIDITY | - | 30 | 60 | - | I2+/I2- | XAI4-5 | XAI4-6
28 | IM1 | AI4 | 24VDC | Sink | 0-101 | °C | FIELD | HT-002 | HT-002 | HVAC ROOM HUMIDITY | - | 30 | 60 | - | I3+/I3- | XAI4-7 | XAI4-8
29 | IM1 | AI4 | 24VDC | Sink | 0-102 | °C | FIELD | HT-003 | HT-003 | EQUIPMENT TOOL ROOM HUMIDITY | - | 30 | 60 | - | I4+/I4- | XAI4-9 | XAI4-10
30 | IM1 | AI4 | 24VDC | Sink | 0-103 | °C | FIELD | HT-004 | HT-004 | MACHINE WORKSHOP HUMIDITY | - | 30 | 60 | - | I5+/I5- | XAI4-11 | XAI4-12
31 | IM1 | AI4 | 24VDC | Sink | 0-104 | °C | FIELD | HT-005 | HT-005 | E&I WORKSHOP HUMIDITY | - | 30 | 60 | - | I6+/I6- | XAI4-13 | XAI4-14
32 | IM1 | AI4 | 24VDC | Sink | 0-55 | °C | FIELD | HT-006 | HT-006 | CONSUMABLE STORE HUMIDITY | - | 30 | 60 | - | I7+/I7- | XAI4-15 | XAI4-16
33 | IM1 | AI5 | 24VDC | Sink | 0-55 | °C | FIELD | HT-007 | HT-007 | EU OPERATORS OFFICE HUMIDITY | - | 30 | 60 | - | I0+/I0- | XAI5-1 | XAI5-2
34 | IM1 | AI5 | 24VDC | Sink | 0-55 | °C | FIELD | HT-008 | HT-008 | MAINTENANCE SUPERVISOR OFFICE HUMIDITY | - | 30 | 60 | - | I1+/I1- | XAI5-3 | XAI5-4
35 | IM1 | AI5 | 24VDC | Sink | 0-55 | °C | FIELD | HT-009 | HT-009 | TELECOM F&G ROOM HUMIDITY | - | 30 | 60 | - | I2+/I2- | XAI5-5 | XAI5-6
36 | IM1 | AI5 | 24VDC | Sink | 0-55 | °C | FIELD | HT-010 | HT-010 | MAINTENACE TECHNICIAN OFFICE HUMIDITY | - | 30 | 60 | - | I3+/I3- | XAI5-7 | XAI5-8
37 | IM1 | AI5 | 24VDC | Sink | 0-55 | °C | FIELD | HT-011 | HT-011 | TEA ROOM HUMIDITY | - | 30 | 60 | - | I4+/I4- | XAI5-9 | XAI5-10
38 | IM1 | AI5 | 24VDC | Sink | 0-55 | °C | FIELD | HT-012 | HT-012 | TOILET HUMIDITY | - | 30 | 60 | - | I5+/I5- | XAI5-11 | XAI5-12
39 | IM1 | AI5 | 24VDC | Sink | 0-1560 | rpm | FIELD | - | CHLR1-PMP-SPD-FB | CHILLER-1 WATER PUMP SPEED FEEDBACK | - | - | - | - | I6+/I6- | XAI5-13 | XAI5-14
40 | IM1 | AI5 | 24VDC | Sink | - | - | FIELD | 141-MD-0331 | 141-MD-0331-FB | MODULATING DAMPER MD-0331 POSITION FEEDBACK | - | - | - | - | I7+/I7- | XAI5-15 | XAI5-16
41 | IM1 | AI6 | 24VDC | Sink | - | - | FIELD | 141-MD-0332 | 141-MD-0332-FB | MODULATING DAMPER MD-0332 POSITION FEEDBACK | - | - | - | - | I0+/I0- | XAI6-1 | XAI6-2
42 | IM1 | AI6 | 24VDC | Sink | - | - | FIELD | 141-MD-0333 | 141-MD-0333-FB | MODULATING DAMPER MD-0333 POSITION FEEDBACK | - | - | - | - | I1+/I1- | XAI6-3 | XAI6-4
43 | IM1 | AI6 | 24VDC | Sink | - | - | FIELD | 141-MD-0334 | 141-MD-0334-FB | MODULATING DAMPER MD-0334 POSITION FEEDBACK | - | - | - | - | I2+/I2- | XAI6-5 | XAI6-6
44 | IM1 | AI6 | 24VDC | Sink | - | - | FIELD | 141-MD-0335 | 141-MD-0335-FB | MODULATING DAMPER MD-0335 POSITION FEEDBACK | - | - | - | - | I3+/I3- | XAI6-7 | XAI6-8
45 | IM1 | AI6 | 24VDC | Sink | - | - | FIELD | 141-MD-0336 | 141-MD-0336-FB | MODULATING DAMPER MD-0336 POSITION FEEDBACK | - | - | - | - | I4+/I4- | XAI6-9 | XAI6-10
46 | IM1 | AI6 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I5+/I5- | XAI6-11 | XAI6-12
47 | IM1 | AI6 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I6+/I6- | XAI6-13 | XAI6-14
48 | IM1 | AI6 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I7+/I7- | XAI6-15 | XAI6-16
49 | IM1 | AI7 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I0+/I0- | XAI7-1 | XAI7-2
50 | IM1 | AI7 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I1+/I1- | XAI7-3 | XAI7-4
51 | IM1 | AI7 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I2+/I2- | XAI7-5 | XAI7-6
52 | IM1 | AI7 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I3+/I3- | XAI7-7 | XAI7-8
53 | IM1 | AI7 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I4+/I4- | XAI7-9 | XAI7-10
54 | IM1 | AI7 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I5+/I5- | XAI7-11 | XAI7-12
55 | IM1 | AI7 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I6+/I6- | XAI7-13 | XAI7-14
56 | IM1 | AI7 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I7+/I7- | XAI7-15 | XAI7-16

## AO
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
OPERATING SHELTER
RUWAIS - U.A.E.
[10 empty] | FACILITY NAME: BOROUGE 4 | [5 empty] | COMPANY PROJ. NO. |  | 4700000897
[16 empty] | CONTRACTOR. PROJ. NO. |  | 083118C
| OS-HVAC-CP | [8 empty] | DOCUMENT TITLE: OS HVAC PLC System - I/O List REV 3 | [5 empty] | SUBCONTR. ID |  | -
Sl. No. | IM Module | I/O Detail |  |  |  |  | TO | EQUIPMENT TAG | PLC TAG | Description | Alarm Setpoints |  |  |  | PLC Term. | TB GROUP |  | Verified & Signed
|  | Module | Supply | Type | Range | Unit |  |  |  |  | LL | L | H | HH
ANALOGUE OUTPUT
1 | IM1 | AO1 | 24VDC | 4-20mA | - | - | CHILLER-1 | 002513006600GB001A | CHLR1_TMP_SP | TEMPERATURE SET POINT TO CHILLER-1 | - | - | - | - | Q0+/Q0- | XAO1-1 | XAO1-2
2 | IM1 | AO1 | 24VDC | 4-20mA | - | - | CHILLER-1 | 002513006600GB001A | CHLR1_RA_TMP | RETURN AIR TEMPETATURE TO CHILLER-1 | - | - | - | - | Q1+/Q1- | XAO1-3 | XAO1-4
3 | IM1 | AO1 | 24VDC | 4-20mA | - | - | CHILLER-2 | 002513006600GB001B | CHLR2_TMP_SP | TEMPERATURE SET POINT TO CHILLER-2 | - | - | - | - | Q2+/Q2- | XAO1-5 | XAO1-6
4 | IM1 | AO1 | 24VDC | 4-20mA | - | - | CHILLER-2 | 002513006600GB001B | CHLR2_RA_TMP | RETURN AIR TEMPETATURE TO CHILLER-2 | - | - | - | - | Q3+/Q3- | XAO1-7 | XAO1-8
5 | IM1 | AO2 | 24VDC | 4-20mA | - | - | - | - | CHLR1-PMP-SPD-REF | CHILLER-1 WATER PUMP SPEED SETPOINT | - | - | - | - | Q0+/Q0- | XAO2-1 | XAO2-2
6 | IM1 | AO2 | 24VDC | 4-20mA | - | - | - | 141-MD-0331 | 141-MD-0331-SP | MODULATING DAMPER MD-0331 SETPOINT | - | - | - | - | Q1+/Q1- | XAO2-3 | XAO2-4
7 | IM1 | AO2 | 24VDC | 4-20mA | - | - | - | 141-MD-0332 | 141-MD-0332-SP | MODULATING DAMPER MD-0332 SETPOINT | - | - | - | - | Q2+/Q2- | XAO2-5 | XAO2-6
8 | IM1 | AO2 | 24VDC | 4-20mA | - | - | - | 141-MD-0333 | 141-MD-0333-SP | MODULATING DAMPER MD-0333 SETPOINT | - | - | - | - | Q3+/Q3- | XAO2-7 | XAO2-8
9 | IM1 | AO3 | 24VDC | 4-20mA | - | - | - | 141-MD-0334 | 141-MD-0334-SP | MODULATING DAMPER MD-0334 SETPOINT | - | - | - | - | Q0+/Q0- | XAO3-1 | XAO3-2
10 | IM1 | AO3 | 24VDC | 4-20mA | - | - | - | 141-MD-0335 | 141-MD-0335-SP | MODULATING DAMPER MD-0335 SETPOINT | - | - | - | - | Q1+/Q1- | XAO3-3 | XAO3-4
11 | IM1 | AO3 | 24VDC | 4-20mA | - | - | - | 141-MD-0336 | 141-MD-0336-SP | MODULATING DAMPER MD-0336 SETPOINT | - | - | - | - | Q2+/Q2- | XAO3-5 | XAO3-6
12 | IM1 | AO3 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q3+/Q3- | XAO3-7 | XAO3-8
13 | IM1 | AO4 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q0+/Q0- | XAO4-1 | XAO4-2
14 | IM1 | AO4 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q1+/Q1- | XAO4-3 | XAO4-4
15 | IM1 | AO4 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q2+/Q2- | XAO4-5 | XAO4-6
16 | IM1 | AO4 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q3+/Q3- | XAO4-7 | XAO4-8

## IO Summary
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
OPERATING SHELTER
RUWAIS - U.A.E.
[8 empty] | FACILITY NAME: BOROUGE 4 | COMPANY PROJ. NO. | 4700000897
[9 empty] | CONTRACTOR. PROJ. NO. | 083118C
OS-HVAC-CP | [7 empty] | DOCUMENT TITLE: OS HVAC PLC System - I/O List REV 3 | SUBCONTR. ID | -
IO SUMMARY
Sl.No | Type | No. Of Channels | No. Of Modules | Count | Used | Spare | Spare %
1 | DI | 16 | 10 | 160 | 128 | 32 | 25
3 | DO | 16 | 4 | 64 | 50 | 14 | 28
4 | AI | 8 | 7 | 56 | 45 | 11 | 24.4444
5 | AO | 4 | 4 | 16 | 11 | 5 | 45.4545