## DI
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
OPERATING SHELTER
RUWAIS - U.A.E.
[10 empty] | FACILITY NAME: BOROUGE 4 |  |  |  | COMPANY PROJ. NO. |  | 4700000897
[14 empty] | CONTRACTOR. PROJ. NO. |  | 083118C
|  | SS-01-HVAC-CP | [7 empty] | DOCUMENT TITLE: OS HVAC PLC System - I/O List REV 3 |  |  |  | SUBCONTR. ID |  | -
Sl. No. | IM Module | I/O Detail |  |  |  |  | FROM | EQUIPMENT TAG | PLC TAG | Description | States |  | PLC Term. | TB GROUP |  | Verified & Signed (Remarks)
|  | Module | Supply | Type | Range | Unit |  |  |  |  | FALSE | TRUE
DIGITAL INPUT
1 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 002513006600GB001A | CHLR1_RUN | CHILLER-1 UNIT RUN STATUS | STOPPED | RUNNING | I0.0 | XDI1-1 | XDI1-2
2 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 002513006600GB001A | CHLR1_TRP | CHILLER-1 UNIT TRIP STATUS | NORMAL | TRIP | I0.1 | XDI1-3 | XDI1-4
3 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 002513006600GB001A | CHLR1_RMT | CHILLER-1 REMOTE MODE STATUS | LOCAL | REMOTE | I0.2 | XDI1-5 | XDI1-6
4 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GB001A | CHLR1_BRK_TRP | CHILLER-1 UNIT BREAKER TRIP STATUS | NORMAL | TRIP | I0.3 | XDI1-7 | XDI1-8
5 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 002513006600GB001B | CHLR2_RUN | CHILLER-2 UNIT RUN STATUS | STOPPED | RUNNING | I0.4 | XDI1-9 | XDI1-10
6 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 002513006600GB001B | CHLR2_TRP | CHILLER-2 UNIT TRIP STATUS | NORMAL | TRIP | I0.5 | XDI1-11 | XDI1-12
7 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 002513006600GB001B | CHLR2_RMT | CHILLER-2 REMOTE MODE STATUS | LOCAL | REMOTE | I0.6 | XDI1-13 | XDI1-14
8 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GB001B | CHLR2_BRK_TRP | CHILLER-2 UNIT BREAKER TRIP STATUS | NORMAL | TRIP | I0.7 | XDI1-15 | XDI1-16
9 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA001A | AHU1_RUN | AHU-1 RUN STATUS | STOPPED | RUNNING | I1.4 | XDI1-17 | XDI1-18
10 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA001A | AHU1_TRP | AHU-1 TRIP STATUS | NORMAL | TRIP | I1.5 | XDI1-19 | XDI1-20
11 | IM1 | DI1 | 24VDC | VF | - | - | LCP | 002513006600GA001A | AHU1_RMT | AHU-1 REMOTE MODE STATUS | LOCAL | REMOTE | I1.6 | XDI1-21 | XDI1-22
12 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA001A | AHU1_BRK_TRP | AHU-1 UNIT BREAKER TRIP STATUS | NORMAL | TRIP | I1.7 | XDI1-23 | XDI1-24
13 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 002513006600GA001A | AHU1_PF_DPS | AHU-1 PRE-FILTER DIFFERENTIAL PRESSURE HIGH | NORMAL | ALARM | I2.0 | XDI1-25 | XDI1-26
14 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 002513006600GA001A | AHU1_FF_DPS | AHU-1 FINE-FILTER DIFFERENTIAL PRESSURE HIGH | NORMAL | ALARM | I2.1 | XDI1-27 | XDI1-28
15 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 002513006600GA001A | AHU1_AF_DPS | AHU-1 FAN AIR FLOW DIFFERENTIAL PRESSURE | NO FLOW | FLOW ON | I2.2 | XDI1-29 | XDI1-30
16 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-001 | 002509006600GA001B | AHU2_RUN | AHU-2 RUN STATUS | STOPPED | RUNNING | I3.1 | XDI1-31 | XDI1-32
17 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001 | 002509006600GA001B | AHU2_TRP | AHU-2 TRIP STATUS | NORMAL | TRIP | I3.2 | XDI2-1 | XDI2-2
18 | IM1 | DI2 | 24VDC | VF | - | - | LCP | 002509006600GA001B | AHU2_RMT | AHU-2 REMOTE MODE STATUS | LOCAL | REMOTE | I3.3 | XDI2-3 | XDI2-4
19 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001 | 002509006600GA001B | AHU2_BRK_TRP | AHU-2 UNIT BREAKER TRIP STATUS | NORMAL | TRIP | I3.4 | XDI2-5 | XDI2-6
20 | IM1 | DI2 | 24VDC | VF | - | - | FIELD | 002509006600GA001B | AHU2_PF_DPS | AHU-2 PRE-FILTER DIFFERENTIAL PRESSURE HIGH | NORMAL | ALARM | I3.5 | XDI2-7 | XDI2-8
21 | IM1 | DI2 | 24VDC | VF | - | - | FIELD | 002509006600GA001B | AHU2_FF_DPS | AHU-2 FINE-FILTER DIFFERENTIAL PRESSURE HIGH | NORMAL | ALARM | I3.6 | XDI2-9 | XDI2-10
22 | IM1 | DI2 | 24VDC | VF | - | - | FIELD | 002509006600GA001B | AHU2_AF_DPS | AHU-2 FAN AIR FLOW DIFFERENTIAL PRESSURE | NO FLOW | FLOW ON | I3.7 | XDI2-11 | XDI2-12
23 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006A | BAT_FAN1_RUN | BATTERY ROOM FAN-1 RUN STATUS | STOPPED | RUNNING | I6.3 | XDI2-13 | XDI2-14
24 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006A | BAT_FAN1_TRP | BATTERY ROOM FAN-1 TRIP STATUS | NORMAL | TRIP | I6.4 | XDI2-15 | XDI2-16
25 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006A | BAT_FAN1_RMT | BATTERY ROOM FAN-1 REMOTE MODE STATUS | LOCAL | REMOTE | I6.5 | XDI2-17 | XDI2-18
26 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006A | BAT_FAN1_ES | BATTERY ROOM FAN-1 EMERGENCY STOP | NORMAL | ACTIVE | I6.6 | XDI2-19 | XDI2-20
27 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006B | BAT_FAN2_RUN | BATTERY ROOM FAN-2 RUN STATUS | STOPPED | RUNNING | I6.7 | XDI2-21 | XDI2-22
28 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006B | BAT_FAN2_TRP | BATTERY ROOM FAN-2 TRIP STATUS | NORMAL | TRIP | I7.0 | XDI2-23 | XDI2-24
29 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006B | BAT_FAN2_RMT | BATTERY ROOM FAN-2 REMOTE MODE STATUS | LOCAL | REMOTE | I7.1 | XDI2-25 | XDI2-26
30 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006B | BAT_FAN2_ES | BATTERY ROOM FAN-2 EMERGENCY STOP | NORMAL | ACTIVE | I7.2 | XDI2-27 | XDI2-28
31 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001 |  | BLD_FAN_RUN | BLEED FAN RUN STATUS | STOPPED | RUNNING | I6.3 | XDI2-29 | XDI2-30
32 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001 |  | BLD_FAN_TRP | BLEED FAN TRIP STATUS | NORMAL | TRIP | I6.4 | XDI2-31 | XDI2-32
33 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-001 |  | BLD_FAN_RMT | BLEED FAN REMOTE MODE STATUS | LOCAL | REMOTE | I6.5 | XDI3-1 | XDI3-2
34 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-001 |  | BLD_FAN_ES | BLEED FAN EMERGENCY STOP | NORMAL | ACTIVE | I6.6 | XDI3-3 | XDI3-4
35 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GB001A | CHLR1_PMP_RUN | CHILLER-1 WATER PUMP RUN STATUS | STOPPED | RUNNING | I6.3 | XDI3-5 | XDI3-6
36 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GB001A | CHLR1_PMP_TRP | CHILLER-1 WATER PUMP TRIP STATUS | NORMAL | TRIP | I6.4 | XDI3-7 | XDI3-8
37 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GB001A | CHLR1_PMP_RMT | CHILLER-1 WATER PUMP REMOTE MODE STATUS | LOCAL | REMOTE | I6.5 | XDI3-9 | XDI3-10
38 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GB001A | CHLR1_PMP_ES | CHILLER-1 WATER PUMP EMERGENCY STOP | NORMAL | ACTIVE | I6.6 | XDI3-11 | XDI3-12
39 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GB001B | CHLR2_PMP_RUN | CHILLER-2 WATER PUMP RUN STATUS | STOPPED | RUNNING | I6.3 | XDI3-13 | XDI3-14
40 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GB001B | CHLR2_PMP_TRP | CHILLER-2 WATER PUMP TRIP STATUS | NORMAL | TRIP | I6.4 | XDI3-15 | XDI3-16
41 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GB001B | CHLR2_PMP_RMT | CHILLER-2 WATER PUMP REMOTE MODE STATUS | LOCAL | REMOTE | I6.5 | XDI3-17 | XDI3-18
42 | IM1 | DI3 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GB001B | CHLR2_PMP_ES | CHILLER-2 WATER PUMP EMERGENCY STOP | NORMAL | ACTIVE | I6.6 | XDI3-19 | XDI3-20
43 | IM1 | DI3 | 24VDC | VF | - | - | FIELD |  | 141-GD-0301-ZIO | MOTORIZED GAS DAMPER 141-GD-0301 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI3-21 | XDI3-22
44 | IM1 | DI3 | 24VDC | VF | - | - | FIELD |  | 141-GD-0301-ZIC | MOTORIZED GAS DAMPER 141-GD-0301 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI3-23 | XDI3-24
45 | IM1 | DI3 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0302-ZIO | MOTORIZED GAS DAMPER 141-MFD-0302 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI3-25 | XDI3-26
46 | IM1 | DI3 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0302-ZIC | MOTORIZED GAS DAMPER 141-MFD-0302 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI3-27 | XDI3-28
47 | IM1 | DI3 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0303-ZIO | MOTORIZED GAS DAMPER 141-MFD-0303 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI3-29 | XDI3-30
48 | IM1 | DI3 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0303-ZIC | MOTORIZED GAS DAMPER 141-MFD-0303 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI3-31 | XDI3-32
49 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0304-ZIO | MOTORIZED GAS DAMPER 141-MFD-0304 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI4-1 | XDI4-2
50 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0304-ZIC | MOTORIZED GAS DAMPER 141-MFD-0304 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI4-3 | XDI4-4
51 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0305-ZIO | MOTORIZED GAS DAMPER 141-MFD-0305 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI4-5 | XDI4-6
52 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0305-ZIC | MOTORIZED GAS DAMPER 141-MFD-0305 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI4-7 | XDI4-8
53 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0306-ZIO | MOTORIZED GAS DAMPER 141-MFD-0306 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI4-9 | XDI4-10
54 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0306-ZIC | MOTORIZED GAS DAMPER 141-MFD-0306 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI4-11 | XDI4-12
55 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0307-ZIO | MOTORIZED GAS DAMPER 141-MFD-0307 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI4-13 | XDI4-14
56 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0307-ZIC | MOTORIZED GAS DAMPER 141-MFD-0307 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI4-15 | XDI4-16
57 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0308-ZIO | MOTORIZED GAS DAMPER 141-MFD-0308 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI4-17 | XDI4-18
58 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0308-ZIC | MOTORIZED GAS DAMPER 141-MFD-0308 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI4-19 | XDI4-20
59 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0309-ZIO | MOTORIZED GAS DAMPER 141-MFD-0309 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI4-21 | XDI4-22
60 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0309-ZIC | MOTORIZED GAS DAMPER 141-MFD-0309 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI4-23 | XDI4-24
61 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0310-ZIO | MOTORIZED GAS DAMPER 141-MFD-0310 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI4-25 | XDI4-26
62 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0310-ZIC | MOTORIZED GAS DAMPER 141-MFD-0310 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI4-27 | XDI4-28
63 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0311-ZIO | MOTORIZED GAS DAMPER 141-MFD-0311 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI4-29 | XDI4-30
64 | IM1 | DI4 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0311-ZIC | MOTORIZED GAS DAMPER 141-MFD-0311 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI4-31 | XDI4-32
65 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0312-ZIO | MOTORIZED GAS DAMPER 141-MFD-0312 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI5-1 | XDI5-2
66 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0312-ZIC | MOTORIZED GAS DAMPER 141-MFD-0312 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI5-3 | XDI5-4
67 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0313-ZIO | MOTORIZED GAS DAMPER 141-MFD-0313 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI5-5 | XDI5-6
68 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0313-ZIC | MOTORIZED GAS DAMPER 141-MFD-0313 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI5-7 | XDI5-8
69 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0314-ZIO | MOTORIZED GAS DAMPER 141-MFD-0314 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI5-9 | XDI5-10
70 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0314-ZIC | MOTORIZED GAS DAMPER 141-MFD-0314 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI5-11 | XDI5-12
71 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0315-ZIO | MOTORIZED GAS DAMPER 141-MFD-0315 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI5-13 | XDI5-14
72 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0315-ZIC | MOTORIZED GAS DAMPER 141-MFD-0315 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI5-15 | XDI5-16
73 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0316-ZIO | MOTORIZED GAS DAMPER 141-MFD-0316 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI5-17 | XDI5-18
74 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0316-ZIC | MOTORIZED GAS DAMPER 141-MFD-0316 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI5-19 | XDI5-20
75 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0317-ZIO | MOTORIZED GAS DAMPER 141-MFD-0317 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI5-21 | XDI5-22
76 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0317-ZIC | MOTORIZED GAS DAMPER 141-MFD-0317 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI5-23 | XDI5-24
77 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0318-ZIO | MOTORIZED GAS DAMPER 141-MFD-0318 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI5-25 | XDI5-26
78 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0318-ZIC | MOTORIZED GAS DAMPER 141-MFD-0318 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI5-27 | XDI5-28
79 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0319-ZIO | MOTORIZED GAS DAMPER 141-MFD-0319 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI5-29 | XDI5-30
80 | IM1 | DI5 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0319-ZIC | MOTORIZED GAS DAMPER 141-MFD-0319 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI5-31 | XDI5-32
81 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0320-ZIO | MOTORIZED GAS DAMPER 141-MFD-0320 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI6-1 | XDI6-2
82 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0320-ZIC | MOTORIZED GAS DAMPER 141-MFD-0320 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI6-3 | XDI6-4
83 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0321-ZIO | MOTORIZED GAS DAMPER 141-MFD-0321 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI6-5 | XDI6-6
84 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0321-ZIC | MOTORIZED GAS DAMPER 141-MFD-0321 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI6-7 | XDI6-8
85 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0322-ZIO | MOTORIZED GAS DAMPER 141-MFD-0322 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI6-9 | XDI6-10
86 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0322-ZIC | MOTORIZED GAS DAMPER 141-MFD-0322 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI6-11 | XDI6-12
87 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0323-ZIO | MOTORIZED GAS DAMPER 141-MFD-0323 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI6-13 | XDI6-14
88 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0323-ZIC | MOTORIZED GAS DAMPER 141-MFD-0323 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI6-15 | XDI6-16
89 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0324-ZIO | MOTORIZED GAS DAMPER 141-MFD-0324 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI6-17 | XDI6-18
90 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0324-ZIC | MOTORIZED GAS DAMPER 141-MFD-0324 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI6-19 | XDI6-20
91 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0325-ZIO | MOTORIZED GAS DAMPER 141-MFD-0325 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI6-21 | XDI6-22
92 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0325-ZIC | MOTORIZED GAS DAMPER 141-MFD-0325 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI6-23 | XDI6-24
93 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0326-ZIO | MOTORIZED GAS DAMPER 141-MFD-0326 OPEN FEEDBACK | NOT OPEN | OPEN | I9.6 | XDI6-25 | XDI6-26
94 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | 141-MFD-0326-ZIC | MOTORIZED GAS DAMPER 141-MFD-0326 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I9.7 | XDI6-27 | XDI6-28
95 | IM1 | DI6 | 24VDC | VF | - | - | FIELD | 002513006600GB001A | CHLR1-BFV-ZIO | MOTORIZED BUTTER FLY VALVE CHILLER-1 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI6-29 | XDI6-30
96 | IM1 | DI6 | 24VDC | VF | - | - | FIELD | 002513006600GB001A | CHLR1-BFV-ZIC | MOTORIZED BUTTER FLY VALVE CHILLER-1 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI6-31 | XDI6-32
97 | IM1 | DI7 | 24VDC | VF | - | - | FIELD | 002513006600GB001B | CHLR2-BFV-ZIO | MOTORIZED BUTTER FLY VALVE CHILLER-2 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI7-1 | XDI7-2
98 | IM1 | DI7 | 24VDC | VF | - | - | FIELD | 002513006600GB001B | CHLR2-BFV-ZIC | MOTORIZED BUTTER FLY VALVE CHILLER-2 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI7-3 | XDI7-4
99 | IM1 | DI7 | 24VDC | VF | - | - | FIELD | 002513006600GA006A | BAT_FAN1_DPS | DIFFERENTIAL PRESSURE ACROSS BATTERY ROOM FAN-1 | NO FLOW | FLOW ON | I9.6 | XDI7-5 | XDI7-6
100 | IM1 | DI7 | 24VDC | VF | - | - | FIELD | 002513006600GA006B | BAT_FAN2_DPS | DIFFERENTIAL PRESSURE ACROSS BATTERY ROOM FAN-2 | NO FLOW | FLOW ON | I9.7 | XDI7-7 | XDI7-8
101 | IM1 | DI7 | 24VDC | VF | - | - | FIELD |  | MW_HTR_TRP | MACHINE WORKSHOP HEATER TRIP STATUS | NORMAL | TRIP | I9.6 | XDI7-9 | XDI7-10
102 | IM1 | DI7 | 24VDC | VF | - | - | FIELD |  | EIW_HTR_TRP | E&I WORKSHOP HEATER TRIP STATUS | NORMAL | TRIP | I9.7 | XDI7-11 | XDI7-12
103 | IM1 | DI7 | 24VDC | VF | - | - | FIELD |  | MTO_HTR_TRP | MAINTENANCE TECHNICIAN OFFICE HEATER TRIP STATUS | NORMAL | TRIP | I11.6 | XDI7-13 | XDI7-14
104 | IM1 | DI7 | 24VDC | VF | - | - | FIELD |  | TLR_HTR_TRP | TELECOM ROOM HEATER TRIP STATUS | NORMAL | TRIP | I11.7 | XDI7-15 | XDI7-16
105 | IM1 | DI7 | 24VDC | VF | - | - | FIELD |  | MSU_HTR_TRP | MAINTENANCE SUPERVISOR OFFICE HEATER TRIP STATUS | NORMAL | TRIP | I12.2 | XDI7-17 | XDI7-18
106 | IM1 | DI7 | 24VDC | VF | - | - | FIELD |  | EUO_HTR_TRP | EU OPERATORS OFFICE HEATER TRIP STATUS | NORMAL | TRIP | I12.2 | XDI7-19 | XDI7-20
107 | IM1 | DI7 | 24VDC | VF | - | - | FIELD |  | TR_HTR_TRP | TEA ROOM HEATER TRIP STATUS | NORMAL | TRIP | I12.2 | XDI7-21 | XDI7-22
108 | IM1 | DI7 | 24VDC | VF | - | - | FIELD |  | MW_HTR_xxx | MACHINE WORKSHOP HEATER ON/OFF STATUS | NORMAL | TRIP | I12.2 | XDI7-23 | XDI7-24
109 | IM1 | DI7 | 24VDC | VF | - | - | FIELD |  | EIW_HTR_xxx | E&I WORKSHOP HEATER ON/OFF STATUS | NORMAL | TRIP | I12.3 | XDI7-25 | XDI7-26
110 | IM1 | DI7 | 24VDC | VF | - | - | FIELD |  | MTO_HTR_xxx | MAINTENANCE TECHNICIAN OFFICE HEATER ON/OFF STATUS | NORMAL | TRIP | I12.4 | XDI7-27 | XDI7-28
111 | IM1 | DI7 | 24VDC | VF | - | - | FIELD |  | TLR_HTR_xxx | TELECOM ROOM HEATER ON/OFF STATUS | NORMAL | TRIP | I12.4 | XDI7-29 | XDI7-30
112 | IM1 | DI7 | 24VDC | VF | - | - | FIELD |  | MSU_HTR_xxx | MAINTENANCE SUPERVISOR OFFICE HEATER ON/OFF STATUS | NORMAL | TRIP | I12.2 | XDI7-31 | XDI7-32
113 | IM1 | DI8 | 24VDC | VF | - | - | FIELD |  | EUO_HTR_xxx | EU OPERATORS OFFICE HEATER ON/OFF STATUS | NORMAL | TRIP | I12.2 | XDI8-1 | XDI8-2
114 | IM1 | DI8 | 24VDC | VF | - | - | FIELD |  | TR_HTR_xxx | TEA ROOM HEATER ON/OFF STATUS | NORMAL | TRIP | I12.2 | XDI8-3 | XDI8-4
115 | IM1 | DI8 | 24VDC | VF | - | - | 141-EC-0001 | - | EMG_STP | HVACP EMERGENCY STOP | NORMAL | ACTIVE | I12.2 | XDI8-5 | XDI8-6
116 | IM1 | DI8 | 24VDC | VF | - | - | 141-EC-0001 | - | MUTE_PB | MUTE PUSH BUTTON | OFF | ON | I12.2 | XDI8-7 | XDI8-8
117 | IM1 | DI8 | 24VDC | VF | - | - | 141-EC-0001 | - | RST_PB | RESET PUSH BUTTON | OFF | ON | I12.2 | XDI8-9 | XDI8-10
118 | IM1 | DI8 | 24VDC | VF | - | - | 141-EC-0001 | - | PSU1&2_HLTHY | POWER SUPPLY 1 & 2 HEALTHY | UNHEALTHY | HEALTHY | I12.2 | XDI8-11 | XDI8-12
119 | IM1 | DI8 | 24VDC | VF | - | - | 141-EC-0001 | - | AFS_HLTHY | PANEL AIR FLOW SWITCH HEALTHY | UNHEALTHY | HEALTHY | I13.1 | XDI8-13 | XDI8-14
120 | IM1 | DI8 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I13.2 | XDI8-15 | XDI8-16
121 | IM1 | DI8 | 24VDC | VF | - | - | LFCP |  | HVAC_SHUT | HVAC SHUTDOWN COMMAND FROM F&G AND ALL DAMPERS CLOSE | NORMAL | SHUTDOWN | I13.4 | XDI8-17 | XDI8-18
122 | IM1 | DI8 | 24VDC | VF | - | - | LFCP |  | HVAC_RECR | HVAC RECIRCULATION MODE FROM F&G AIR INTAKE DAMPER CLOSE | NORMAL | RECIRCUL | I13.5 | XDI8-19 | XDI8-20
123 | IM1 | DI8 | 24VDC | VF | - | - | LFCP |  | LFCP_ZONE1 | LFCP ZONE 1 SELECTION | NOT SELECTED | SELECTED | I13.6 | XDI8-21 | XDI8-22
124 | IM1 | DI8 | 24VDC | VF | - | - | LFCP | - | LFCP_ZONE2 | LFCP ZONE 2 SELECTION | NOT SELECTED | SELECTED | I13.7 | XDI8-23 | XDI8-24
125 | IM1 | DI8 | 24VDC | VF | - | - | LFCP | - | LFCP_ZONE3 | LFCP ZONE 3 SELECTION | NOT SELECTED | SELECTED | I14.0 | XDI8-25 | XDI8-26
126 | IM1 | DI8 | 24VDC | VF | - | - | LFCP | - | LFCP_ZONE4 | LFCP ZONE 4 SELECTION | NOT SELECTED | SELECTED | I14.1 | XDI8-27 | XDI8-28
127 | IM1 | DI8 | 24VDC | VF | - | - | LFCP | - | LFCP_ZONE5 | LFCP ZONE 5 SELECTION | NOT SELECTED | SELECTED | I14.2 | XDI8-29 | XDI8-30
128 | IM1 | DI8 | 24VDC | VF | - | - | LFCP | - | LFCP_ZONE6 | LFCP ZONE 6 SELECTION | NOT SELECTED | SELECTED | I14.3 | XDI8-31 | XDI8-32
129 | IM1 | DI9 | 24VDC | VF | - | - | LFCP | - | LFCP_ZONE7 | LFCP ZONE 7 SELECTION | NOT SELECTED | SELECTED | I14.4 | XDI9-1 | XDI9-2
130 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I14.5 | XDI9-3 | XDI9-4
131 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I14.6 | XDI9-5 | XDI9-6
132 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I14.7 | XDI9-7 | XDI9-8
133 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I15.0 | XDI9-9 | XDI9-10
134 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I15.1 | XDI9-11 | XDI9-12
135 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I15.2 | XDI9-13 | XDI9-14
136 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I15.3 | XDI9-15 | XDI9-16
137 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I15.4 | XDI9-17 | XDI9-18
138 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I15.5 | XDI9-19 | XDI9-20
139 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I15.6 | XDI9-21 | XDI9-22
140 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I15.7 | XDI9-23 | XDI9-24
141 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I16.0 | XDI9-25 | XDI9-26
142 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I16.1 | XDI9-27 | XDI9-28
143 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I16.2 | XDI9-29 | XDI9-30
144 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I16.3 | XDI9-31 | XDI9-32
145 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I16.4 | XDI10-1 | XDI10-2
146 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I16.5 | XDI10-3 | XDI10-4
147 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I16.6 | XDI10-5 | XDI10-6
148 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I16.7 | XDI10-7 | XDI10-8
149 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.0 | XDI10-9 | XDI10-10
150 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.1 | XDI10-11 | XDI10-12
151 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.2 | XDI10-13 | XDI10-14
152 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.3 | XDI10-15 | XDI10-16
153 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.4 | XDI10-17 | XDI10-18
154 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.5 | XDI10-19 | XDI10-20
155 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.6 | XDI10-21 | XDI10-22
156 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.7 | XDI10-23 | XDI10-24
157 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.2 | XDI10-25 | XDI10-26
158 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.3 | XDI10-27 | XDI10-28
159 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.4 | XDI10-29 | XDI10-30
160 | IM1 | DI10 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.5 | XDI10-31 | XDI10-32

## DO
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
OPERATING SHELTER
RUWAIS - U.A.E.
[10 empty] | FACILITY NAME: BOROUGE 4 |  |  |  | COMPANY PROJ. NO. |  | 4700000897
[14 empty] | CONTRACTOR. PROJ. NO. |  | 083118C
|  | SS-01-HVAC-CP | [7 empty] | DOCUMENT TITLE: OS HVAC PLC System - I/O List REV 3 |  |  |  | SUBCONTR. ID |  | -
Sl. No. | IM Module | I/O Detail |  |  |  |  | TO | EQUIPMENT TAG | PLC TAG | Description | STATES |  | PLC Term. | TB GROUP |  | Verified & Signed
|  | Module | Supply | Type | Range | Unit |  |  |  |  | FALSE | TRUE
DIGITAL OUTPUT
1 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GB001A | CHLR1_CMD | CHILLER-1 START/STOP COMMAND | STOP | START | Q0.0 | XDO1-1 | XDO1-2
2 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GB001B | CHLR2_CMD | CHILLER-2 START/STOP COMMAND | STOP | START | Q0.1 | XDO1-3 | XDO1-4
3 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA001A | AHU1_CMD | AHU-1 START/STOP COMMAND | STOP | START | Q0.3 | XDO1-5 | XDO1-6
4 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002509006600GA001B | AHU2_CMD | AHU-2 START/STOP COMMAND | STOP | START | Q0.4 | XDO1-7 | XDO1-8
5 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006A | BAT_FAN1_CMD | BATTERY ROOM EXHAUST FAN-1 START/STOP COMMAND | STOP | START | Q1.2 | XDO1-9 | XDO1-10
6 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006A | BAT_FAN2_CMD | BATTERY ROOM EXHAUST FAN-2 START/STOP COMMAND | STOP | START | Q1.2 | XDO1-11 | XDO1-12
7 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006A | CHLR1_BFV_OPN | CHILLER-1 MOTORIZED BUTTER FLY VALVE OPEN COMMAND | NOT OPEN | OPEN | Q1.2 | XDO1-13 | XDO1-14
8 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006A | CHLR1_BFV_CLS | CHILLER-1 MOTORIZED BUTTER FLY VALVE CLOSE COMMAND | NOT CLOSE | CLOSE | Q1.2 | XDO1-15 | XDO1-16
9 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006A | CHLR2_BFV_OPN | CHILLER-2 MOTORIZED BUTTER FLY VALVE OPEN COMMAND | NOT OPEN | OPEN | Q1.2 | XDO1-17 | XDO1-18
10 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006A | CHLR2_BFV_CLS | CHILLER-2 MOTORIZED BUTTER FLY VALVE CLOSE COMMAND | NOT CLOSE | CLOSE | Q1.2 | XDO1-19 | XDO1-20
11 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006A | CHLR1_PMP_CMD | CHILLER-1 WATER PUMP START/STOP COMMAND | STOP | START | Q1.2 | XDO1-21 | XDO1-22
12 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GA006A | CHLR2_PMP_CMD | CHILLER-2 WATER PUMP START/STOP COMMAND | STOP | START | Q1.2 | XDO1-23 | XDO1-24
13 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GT001 | MW_HTR_CMD | MACHINE WORKSHOP HEATER ON/OFF COMMAND | OFF | ON | Q1.4 | XDO1-25 | XDO1-26
14 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GT001 | EIW_HTR_CMD | E&I WORKSHOP HEATER ON/OFF COMMAND | OFF | ON | Q1.4 | XDO1-27 | XDO1-28
15 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GT001 | MTO_HTR_CMD | MAINTENANCE TECHNICIAN OFFICE HEATER ON/OFF COMMAND | OFF | ON | Q1.4 | XDO1-29 | XDO1-30
16 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GT002 | TLR_HTR_CMD | TELECOM ROOM HEATER ON/OFF COMMAND | OFF | ON | Q1.5 | XDO1-31 | XDO1-32
17 | IM1 | DO2 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GT001 | MSU_HTR_CMD | MAINTENANCE SUPERVISOR OFFICE HEATER ON/OFF COMMAND | OFF | ON | Q1.4 | XDO2-1 | XDO2-2
18 | IM1 | DO2 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GT001 | EUO_HTR_CMD | EU OPERATORS OFFICE HEATER ON/OFF COMMAND | OFF | ON | Q1.4 | XDO2-3 | XDO2-4
19 | IM1 | DO2 | 24VDC | VF | - | - | 141-ES-001 | 002513006600GT001 | TR_HTR_CMD | TEA ROOM HEATER ON/OFF COMMAND | OFF | ON | Q1.4 | XDO2-5 | XDO2-6
20 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-GD-0301 | 141-GD-0301-CMD | MOTORIZED GAS DAMPER 141-GD-0301 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-7 | XDO2-8
21 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0302 | 141-MFD-0302-CMD | MOTORIZED FIRE DAMPER 141-MFD-0302 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-9 | XDO2-10
22 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0303 | 141-MFD-0303-CMD | MOTORIZED FIRE DAMPER 141-MFD-0303 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-11 | XDO2-12
23 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0304 | 141-MFD-0304-CMD | MOTORIZED FIRE DAMPER 141-MFD-0304 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-13 | XDO2-14
24 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0305 | 141-MFD-0305-CMD | MOTORIZED FIRE DAMPER 141-MFD-0305 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-15 | XDO2-16
25 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0306 | 141-MFD-0306-CMD | MOTORIZED FIRE DAMPER 141-MFD-0306 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-17 | XDO2-18
26 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0307 | 141-MFD-0307-CMD | MOTORIZED FIRE DAMPER 141-MFD-0307 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-19 | XDO2-20
27 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0308 | 141-MFD-0308-CMD | MOTORIZED FIRE DAMPER 141-MFD-0308 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-21 | XDO2-22
28 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0309 | 141-MFD-0309-CMD | MOTORIZED FIRE DAMPER 141-MFD-0309 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-23 | XDO2-24
29 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0310 | 141-MFD-0310-CMD | MOTORIZED FIRE DAMPER 141-MFD-0310 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-25 | XDO2-26
30 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0311 | 141-MFD-0311-CMD | MOTORIZED FIRE DAMPER 141-MFD-0311 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-27 | XDO2-28
31 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0312 | 141-MFD-0312-CMD | MOTORIZED FIRE DAMPER 141-MFD-0312 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-29 | XDO2-30
32 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-MFD-0313 | 141-MFD-0313-CMD | MOTORIZED FIRE DAMPER 141-MFD-0313 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-31 | XDO2-32
33 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-MFD-0314 | 141-MFD-0314-CMD | MOTORIZED FIRE DAMPER 141-MFD-0314 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-1 | XDO3-2
34 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-MFD-0315 | 141-MFD-0315-CMD | MOTORIZED FIRE DAMPER 141-MFD-0315 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-3 | XDO3-4
35 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-MFD-0316 | 141-MFD-0316-CMD | MOTORIZED FIRE DAMPER 141-MFD-0316 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-5 | XDO3-6
36 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-MFD-0317 | 141-MFD-0317-CMD | MOTORIZED FIRE DAMPER 141-MFD-0317 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-7 | XDO3-8
37 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-MFD-0318 | 141-MFD-0318-CMD | MOTORIZED FIRE DAMPER 141-MFD-0318 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-9 | XDO3-10
38 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-MFD-0319 | 141-MFD-0319-CMD | MOTORIZED FIRE DAMPER 141-MFD-0319 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-11 | XDO3-12
39 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-MFD-0320 | 141-MFD-0320-CMD | MOTORIZED FIRE DAMPER 141-MFD-0320 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-13 | XDO3-14
40 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-MFD-0321 | 141-MFD-0321-CMD | MOTORIZED FIRE DAMPER 141-MFD-0321 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-15 | XDO3-16
41 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-MFD-0322 | 141-MFD-0322-CMD | MOTORIZED FIRE DAMPER 141-MFD-0322 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-17 | XDO3-18
42 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-MFD-0323 | 141-MFD-0323-CMD | MOTORIZED FIRE DAMPER 141-MFD-0323 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-19 | XDO3-20
43 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-MFD-0324 | 141-MFD-0324-CMD | MOTORIZED FIRE DAMPER 141-MFD-0324 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-21 | XDO3-22
44 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-MFD-0325 | 141-MFD-0325-CMD | MOTORIZED FIRE DAMPER 141-MFD-0325 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-23 | XDO3-24
45 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-MFD-0326 | 141-MFD-0326-CMD | MOTORIZED FIRE DAMPER 141-MFD-0326 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-25 | XDO3-26
46 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-GD-0137 | 141-GD-0334-CMD | MOTORIZED GAS DAMPER 141-GD-0334 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-27 | XDO3-28
47 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-GD-0137 | 141-GD-0336-CMD | MOTORIZED GAS DAMPER 141-GD-0336 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-29 | XDO3-30
48 | IM1 | DO3 | 24VDC | VF | - | - | F&G | - | HVAC_SHUT_FG | HVAC SHUTDOWN/DAMPER CLOSE FEEDBACK TO F&G | OFF | ON | Q4.7 | XDO3-31 | XDO3-32
49 | IM1 | DO4 | 24VDC | VF | - | - | F&G | - | HVAC_SHUT_FG | RECIRCULATION/DAMPER CLOSE FEEDBACK TO F&G | OFF | ON | Q4.7 | XDO4-1 | XDO4-2
50 | IM1 | DO4 | 24VDC | VF | - | - | PLC | - | BUZZ_ON | BUZZER ON COMMAND | OFF | ON | Q5.0 | XDO4-3 | XDO4-4
51 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE |  |  | Q4.1 | XDO4-5 | XDO4-6
52 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE |  |  | Q4.2 | XDO4-7 | XDO4-8
53 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE |  |  | Q4.3 | XDO4-9 | XDO4-10
54 | IM1 | DO4 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | Q1.7 | XDO4-11 | XDO4-12
55 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE |  |  | Q2.0 | XDO4-13 | XDO4-14
56 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE |  |  | Q2.1 | XDO4-15 | XDO4-16
57 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE |  |  | Q2.2 | XDO4-17 | XDO4-18
58 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE |  |  | Q2.3 | XDO4-19 | XDO4-20
59 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE |  |  | Q2.4 | XDO4-21 | XDO4-22
60 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE |  |  | Q2.5 | XDO4-23 | XDO4-24
61 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE |  |  | Q2.6 | XDO4-25 | XDO4-26
62 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE |  |  | Q2.7 | XDO4-27 | XDO4-28
63 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE |  |  | Q3.0 | XDO4-29 | XDO4-30
64 | IM1 | DO4 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | Q5.1 | XDO4-31 | XDO4-32

## AI
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
OPERATING SHELTER
RUWAIS - U.A.E.
[10 empty] | FACILITY NAME: BOROUGE 4 | [5 empty] | COMPANY PROJ. NO. |  | 4700000897
[16 empty] | CONTRACTOR. PROJ. NO. |  | 083118C
| SS-01-HVAC-CP | [8 empty] | DOCUMENT TITLE: OS HVAC PLC System - I/O List REV 3 | [5 empty] | SUBCONTR. ID |  | -
Sl. No. | IM Module | I/O Detail |  |  |  |  | FROM | EQUIPMENT TAG | PLC TAG | Description | Alarm Setpoints |  |  |  | PLC Term. | TB GROUP |  | Verified & Signed
|  | Module | Supply | Type | Range | Unit |  |  |  |  | LL | L | H | HH
ANALOGUE INPUT
1 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-1 | DPIT-1 | DIFFERENTIAL PRESSURE HVAC ROOM | - | 1 | 5 | - | I0+/I0- | XAI1-1 | XAI1-2
2 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-2 | DPIT-2 | DIFFERENTIAL PRESSURE EQUIPMENT TOOL ROOM | - | 1 | 5 | - | I1+/I1- | XAI1-3 | XAI1-4
3 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-3 | DPIT-3 | DIFFERENTIAL PRESSURE MACHINE WORKSHOP | - | 1 | 5 | - | I2+/I2- | XAI1-5 | XAI1-6
4 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-4 | DPIT-4 | DIFFERENTIAL PRESSURE E&I WORKSHOP | - | 1 | 5 | - | I3+/I3- | XAI1-7 | XAI1-8
5 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-5 | DPIT-5 | DIFFERENTIAL PRESSURE E&I WORKSHOP AIRLOCK | - | 1 | 5 | - | I4+/I4- | XAI1-9 | XAI1-10
6 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-6 | DPIT-6 | DIFFERENTIAL PRESSURE CONSUMABLE STORE | - | 1 | 5 | - | I5+/I5- | XAI1-11 | XAI1-12
7 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-7 | DPIT-7 | DIFFERENTIAL PRESSURE EU OPERATORS OFFICE | - | 1 | 5 | - | I6+/I6- | XAI1-13 | XAI1-14
8 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-8 | DPIT-8 | DIFFERENTIAL PRESSURE MAINTENANCE SUPERVISOR OFFICE | - | 1 | 5 | - | I7+/I7- | XAI1-15 | XAI1-16
9 | IM1 | AI2 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-9 | DPIT-9 | DIFFERENTIAL PRESSURE TELECOM F&G ROOM | - | 1 | 5 | - | I0+/I0- | XAI2-1 | XAI2-2
10 | IM1 | AI2 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-10 | DPIT-10 | DIFFERENTIAL PRESSURE TELECOM F&G ROOM AIRLOCK | - | 1 | 5 | - | I1+/I1- | XAI2-3 | XAI2-4
11 | IM1 | AI2 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-11 | DPIT-11 | DIFFERENTIAL PRESSURE MAINTENACE TECHNICIAN OFFICE | - | 1 | 5 | - | I2+/I2- | XAI2-5 | XAI2-6
12 | IM1 | AI2 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-12 | DPIT-12 | DIFFERENTIAL PRESSURE TEA ROOM | - | 1 | 5 | - | I3+/I3- | XAI2-7 | XAI2-8
13 | IM1 | AI2 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-13 | DPIT-13 | DIFFERENTIAL PRESSURE TOILET | - | 1 | 5 | - | I4+/I4- | XAI2-9 | XAI2-10
14 | IM1 | AI2 | 24VDC | Sink | 0-55 | °C | FIELD | TT-001 | TT-001 | FRESH AIR DUCT TEMPERATURE | - | 20 | 30 | - | I5+/I5- | XAI2-11 | XAI2-12
15 | IM1 | AI2 | 24VDC | Sink | 0-55 | °C | FIELD | TT-002 | TT-002 | SUPPLY AIR DUCT TEMPERATURE | - | 20 | 30 | - | I6+/I6- | XAI2-13 | XAI2-14
16 | IM1 | AI2 | 24VDC | Sink | 0-55 | °C | FIELD | TT-003 | TT-003 | HVAC ROOM TEMPERATURE | - | 20 | 30 | - | I7+/I7- | XAI2-15 | XAI2-16
17 | IM1 | AI3 | 24VDC | Sink | 0-55 | °C | FIELD | TT-004 | TT-004 | EQUIPMENT TOOL ROOM TEMPERATURE | - | 20 | 30 | - | I0+/I0- | XAI3-1 | XAI3-2
18 | IM1 | AI3 | 24VDC | Sink | 0-55 | °C | FIELD | TT-005 | TT-005 | MACHINE WORKSHOP TEMPERATURE | - | 20 | 30 | - | I1+/I1- | XAI3-3 | XAI3-4
19 | IM1 | AI3 | 24VDC | Sink | 0-55 | °C | FIELD | TT-006 | TT-006 | E&I WORKSHOP TEMPERATURE | - | 20 | 30 | - | I2+/I2- | XAI3-5 | XAI3-6
20 | IM1 | AI3 | 24VDC | Sink | 0-55 | °C | FIELD | TT-007 | TT-007 | CONSUMABLE STORE TEMPERATURE | - | 20 | 30 | - | I3+/I3- | XAI3-7 | XAI3-8
21 | IM1 | AI3 | 24VDC | Sink | 0-55 | °C | FIELD | TT-008 | TT-008 | EU OPERATORS OFFICE TEMPERATURE | - | 20 | 30 | - | I4+/I4- | XAI3-9 | XAI3-10
22 | IM1 | AI3 | 24VDC | Sink | 0-55 | °C | FIELD | TT-009 | TT-009 | MAINTENANCE SUPERVISOR OFFICE TEMPERATURE | - | 20 | 30 | - | I5+/I5- | XAI3-11 | XAI3-12
23 | IM1 | AI3 | 24VDC | Sink | 0-55 | °C | FIELD | TT-010 | TT-010 | TELECOM F&G ROOM TEMPERATURE | - | 20 | 30 | - | I6+/I6- | XAI3-13 | XAI3-14
24 | IM1 | AI3 | 24VDC | Sink | 0-55 | °C | FIELD | TT-011 | TT-011 | MAINTENACE TECHNICIAN OFFICE TEMPERATURE | - | 20 | 30 | - | I7+/I7- | XAI3-15 | XAI3-16
25 | IM1 | AI4 | 24VDC | Sink | 0-55 | °C | FIELD | TT-012 | TT-012 | TEA ROOM TEMPERATURE | - | 20 | 30 | - | I0+/I0- | XAI4-1 | XAI4-2
26 | IM1 | AI4 | 24VDC | Sink | 0-55 | °C | FIELD | TT-013 | TT-013 | TOILET TEMPERATURE | - | 20 | 30 | - | I1+/I1- | XAI4-3 | XAI4-4
27 | IM1 | AI4 | 24VDC | Sink | 0-100 | °C | FIELD | HT-001 | HT-001 | SUPPLY AIR DUCT HUMIDITY | - | 30 | 60 | - | I2+/I2- | XAI4-5 | XAI4-6
28 | IM1 | AI4 | 24VDC | Sink | 0-101 | °C | FIELD | HT-002 | HT-002 | HVAC ROOM HUMIDITY | - | 30 | 60 | - | I3+/I3- | XAI4-7 | XAI4-8
29 | IM1 | AI4 | 24VDC | Sink | 0-102 | °C | FIELD | HT-003 | HT-003 | EQUIPMENT TOOL ROOM HUMIDITY | - | 30 | 60 | - | I4+/I4- | XAI4-9 | XAI4-10
30 | IM1 | AI4 | 24VDC | Sink | 0-103 | °C | FIELD | HT-004 | HT-004 | MACHINE WORKSHOP HUMIDITY | - | 30 | 60 | - | I5+/I5- | XAI4-11 | XAI4-12
31 | IM1 | AI4 | 24VDC | Sink | 0-104 | °C | FIELD | HT-005 | HT-005 | E&I WORKSHOP HUMIDITY | - | 30 | 60 | - | I6+/I6- | XAI4-13 | XAI4-14
32 | IM1 | AI4 | 24VDC | Sink | 0-55 | °C | FIELD | HT-006 | HT-006 | CONSUMABLE STORE HUMIDITY | - | 30 | 60 | - | I7+/I7- | XAI4-15 | XAI4-16
33 | IM1 | AI5 | 24VDC | Sink | 0-55 | °C | FIELD | HT-007 | HT-007 | EU OPERATORS OFFICE HUMIDITY | - | 30 | 60 | - | I0+/I0- | XAI5-1 | XAI5-2
34 | IM1 | AI5 | 24VDC | Sink | 0-55 | °C | FIELD | HT-008 | HT-008 | MAINTENANCE SUPERVISOR OFFICE HUMIDITY | - | 30 | 60 | - | I1+/I1- | XAI5-3 | XAI5-4
35 | IM1 | AI5 | 24VDC | Sink | 0-55 | °C | FIELD | HT-009 | HT-009 | TELECOM F&G ROOM HUMIDITY | - | 30 | 60 | - | I2+/I2- | XAI5-5 | XAI5-6
36 | IM1 | AI5 | 24VDC | Sink | 0-55 | °C | FIELD | HT-010 | HT-010 | MAINTENACE TECHNICIAN OFFICE HUMIDITY | - | 30 | 60 | - | I3+/I3- | XAI5-7 | XAI5-8
37 | IM1 | AI5 | 24VDC | Sink | 0-55 | °C | FIELD | HT-011 | HT-011 | TEA ROOM HUMIDITY | - | 30 | 60 | - | I4+/I4- | XAI5-9 | XAI5-10
38 | IM1 | AI5 | 24VDC | Sink | 0-55 | °C | FIELD | HT-012 | HT-012 | TOILET HUMIDITY | - | 30 | 60 | - | I5+/I5- | XAI5-11 | XAI5-12
39 | IM1 | AI5 | 24VDC | Sink | 0-1560 | rpm | FIELD | - | CHLR1-PMP-SPD-FB | CHILLER-1 WATER PUMP SPEED FEEDBACK | - | - | - | - | I6+/I6- | XAI5-13 | XAI5-14
40 | IM1 | AI5 | 24VDC | Sink | - | - | FIELD | 141-MD-0331 | 141-MD-0331-FB | MODULATING DAMPER MD-0331 POSITION FEEDBACK | - | - | - | - | I7+/I7- | XAI5-15 | XAI5-16
41 | IM1 | AI6 | 24VDC | Sink | - | - | FIELD | 141-MD-0332 | 141-MD-0332-FB | MODULATING DAMPER MD-0332 POSITION FEEDBACK | - | - | - | - | I0+/I0- | XAI6-1 | XAI6-2
42 | IM1 | AI6 | 24VDC | Sink | - | - | FIELD | 141-MD-0333 | 141-MD-0333-FB | MODULATING DAMPER MD-0333 POSITION FEEDBACK | - | - | - | - | I1+/I1- | XAI6-3 | XAI6-4
43 | IM1 | AI6 | 24VDC | Sink | - | - | FIELD | 141-MD-0334 | 141-MD-0334-FB | MODULATING DAMPER MD-0334 POSITION FEEDBACK | - | - | - | - | I2+/I2- | XAI6-5 | XAI6-6
44 | IM1 | AI6 | 24VDC | Sink | - | - | FIELD | 141-MD-0335 | 141-MD-0335-FB | MODULATING DAMPER MD-0335 POSITION FEEDBACK | - | - | - | - | I3+/I3- | XAI6-7 | XAI6-8
45 | IM1 | AI6 | 24VDC | Sink | - | - | FIELD | 141-MD-0336 | 141-MD-0336-FB | MODULATING DAMPER MD-0336 POSITION FEEDBACK | - | - | - | - | I4+/I4- | XAI6-9 | XAI6-10
46 | IM1 | AI6 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I5+/I5- | XAI6-11 | XAI6-12
47 | IM1 | AI6 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I6+/I6- | XAI6-13 | XAI6-14
48 | IM1 | AI6 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I7+/I7- | XAI6-15 | XAI6-16
49 | IM1 | AI7 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I0+/I0- | XAI7-1 | XAI7-2
50 | IM1 | AI7 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I1+/I1- | XAI7-3 | XAI7-4
51 | IM1 | AI7 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I2+/I2- | XAI7-5 | XAI7-6
52 | IM1 | AI7 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I3+/I3- | XAI7-7 | XAI7-8
53 | IM1 | AI7 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I4+/I4- | XAI7-9 | XAI7-10
54 | IM1 | AI7 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I5+/I5- | XAI7-11 | XAI7-12
55 | IM1 | AI7 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I6+/I6- | XAI7-13 | XAI7-14
56 | IM1 | AI7 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I7+/I7- | XAI7-15 | XAI7-16

## AO
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
OPERATING SHELTER
RUWAIS - U.A.E.
[10 empty] | FACILITY NAME: BOROUGE 4 | [5 empty] | COMPANY PROJ. NO. |  | 4700000897
[16 empty] | CONTRACTOR. PROJ. NO. |  | 083118C
| SS-01-HVAC-CP | [8 empty] | DOCUMENT TITLE: OS HVAC PLC System - I/O List REV 3 | [5 empty] | SUBCONTR. ID |  | -
Sl. No. | IM Module | I/O Detail |  |  |  |  | TO | EQUIPMENT TAG | PLC TAG | Description | Alarm Setpoints |  |  |  | PLC Term. | TB GROUP |  | Verified & Signed
|  | Module | Supply | Type | Range | Unit |  |  |  |  | LL | L | H | HH
ANALOGUE OUTPUT
1 | IM1 | AO1 | 24VDC | 4-20mA | - | - | CHILLER-1 | 002513006600GB001A | CHLR1_TMP_SP | TEMPERATURE SET POINT TO CHILLER-1 | - | - | - | - | Q0+/Q0- | XAO1-1 | XAO1-2
2 | IM1 | AO1 | 24VDC | 4-20mA | - | - | CHILLER-1 | 002513006600GB001A | CHLR1_RA_TMP | RETURN AIR TEMPETATURE TO CHILLER-1 | - | - | - | - | Q1+/Q1- | XAO1-3 | XAO1-4
3 | IM1 | AO1 | 24VDC | 4-20mA | - | - | CHILLER-2 | 002513006600GB001B | CHLR2_TMP_SP | TEMPERATURE SET POINT TO CHILLER-2 | - | - | - | - | Q2+/Q2- | XAO1-5 | XAO1-6
4 | IM1 | AO1 | 24VDC | 4-20mA | - | - | CHILLER-2 | 002513006600GB001B | CHLR2_RA_TMP | RETURN AIR TEMPETATURE TO CHILLER-2 | - | - | - | - | Q3+/Q3- | XAO1-7 | XAO1-8
5 | IM1 | AO2 | 24VDC | 4-20mA | - | - | - | - | CHLR1-PMP-SPD-REF | CHILLER-1 WATER PUMP SPEED SETPOINT | - | - | - | - | Q0+/Q0- | XAO2-1 | XAO2-2
6 | IM1 | AO2 | 24VDC | 4-20mA | - | - | - | 141-MD-0331 | 141-MD-0331-SP | MODULATING DAMPER MD-0331 SETPOINT | - | - | - | - | Q1+/Q1- | XAO2-3 | XAO2-4
7 | IM1 | AO2 | 24VDC | 4-20mA | - | - | - | 141-MD-0332 | 141-MD-0332-SP | MODULATING DAMPER MD-0332 SETPOINT | - | - | - | - | Q2+/Q2- | XAO2-5 | XAO2-6
8 | IM1 | AO2 | 24VDC | 4-20mA | - | - | - | 141-MD-0333 | 141-MD-0333-SP | MODULATING DAMPER MD-0333 SETPOINT | - | - | - | - | Q3+/Q3- | XAO2-7 | XAO2-8
9 | IM1 | AO3 | 24VDC | 4-20mA | - | - | - | 141-MD-0334 | 141-MD-0334-SP | MODULATING DAMPER MD-0334 SETPOINT | - | - | - | - | Q0+/Q0- | XAO3-1 | XAO3-2
10 | IM1 | AO3 | 24VDC | 4-20mA | - | - | - | 141-MD-0335 | 141-MD-0335-SP | MODULATING DAMPER MD-0335 SETPOINT | - | - | - | - | Q1+/Q1- | XAO3-3 | XAO3-4
11 | IM1 | AO3 | 24VDC | 4-20mA | - | - | - | 141-MD-0336 | 141-MD-0336-SP | MODULATING DAMPER MD-0336 SETPOINT | - | - | - | - | Q2+/Q2- | XAO3-5 | XAO3-6
12 | IM1 | AO3 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q3+/Q3- | XAO3-7 | XAO3-8
13 | IM1 | AO4 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q0+/Q0- | XAO4-1 | XAO4-2
14 | IM1 | AO4 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q1+/Q1- | XAO4-3 | XAO4-4
15 | IM1 | AO4 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q2+/Q2- | XAO4-5 | XAO4-6
16 | IM1 | AO4 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q3+/Q3- | XAO4-7 | XAO4-8

## IO Summary
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
OPERATING SHELTER
RUWAIS - U.A.E.
[8 empty] | FACILITY NAME: BOROUGE 4 | COMPANY PROJ. NO. | 4700000897
[9 empty] | CONTRACTOR. PROJ. NO. | 083118C
SS-01-HVAC-CP | [7 empty] | DOCUMENT TITLE: OS HVAC PLC System - I/O List REV 3 | SUBCONTR. ID | -
IO SUMMARY
Sl.No | Type | No. Of Channels | No. Of Modules | Count | Used | Spare | Spare %
1 | DI | 16 | 10 | 160 | 128 | 32 | 25
3 | DO | 16 | 4 | 64 | 50 | 14 | 28
4 | AI | 8 | 7 | 56 | 45 | 11 | 24.4444
5 | AO | 4 | 4 | 16 | 11 | 5 | 45.4545

## Sheet1 (hidden)
141-GD-0 | 301 | 141-GD-0301 | 141-GD-0301-CMD | MOTORIZED GAS DAMPER 141-GD-0301 OPEN/CLOSE COMMAND | 141-GD-0301-ZIO | MOTORIZED GAS DAMPER 141-GD-0301 OPEN FEEDBACK
141-GD-0 | 301 | 141-GD-0301 |  |  | 141-GD-0301-ZIC | MOTORIZED GAS DAMPER 141-GD-0301 CLOSE FEEDBACK
141-MFD-0 | 302 | 141-MFD-0302 | 141-MFD-0302-CMD | MOTORIZED FIRE DAMPER 141-MFD-0302 OPEN/CLOSE COMMAND | 141-MFD-0302-ZIO | MOTORIZED GAS DAMPER 141-MFD-0302 OPEN FEEDBACK
141-MFD-0 | 302 | 141-MFD-0302 |  |  | 141-MFD-0302-ZIC | MOTORIZED GAS DAMPER 141-MFD-0302 CLOSE FEEDBACK
141-MFD-0 | 303 | 141-MFD-0303 | 141-MFD-0303-CMD | MOTORIZED FIRE DAMPER 141-MFD-0303 OPEN/CLOSE COMMAND | 141-MFD-0303-ZIO | MOTORIZED GAS DAMPER 141-MFD-0303 OPEN FEEDBACK
141-MFD-0 | 303 | 141-MFD-0303 |  |  | 141-MFD-0303-ZIC | MOTORIZED GAS DAMPER 141-MFD-0303 CLOSE FEEDBACK
141-MFD-0 | 304 | 141-MFD-0304 | 141-MFD-0304-CMD | MOTORIZED FIRE DAMPER 141-MFD-0304 OPEN/CLOSE COMMAND | 141-MFD-0304-ZIO | MOTORIZED GAS DAMPER 141-MFD-0304 OPEN FEEDBACK
141-MFD-0 | 304 | 141-MFD-0304 |  |  | 141-MFD-0304-ZIC | MOTORIZED GAS DAMPER 141-MFD-0304 CLOSE FEEDBACK
141-MFD-0 | 305 | 141-MFD-0305 | 141-MFD-0305-CMD | MOTORIZED FIRE DAMPER 141-MFD-0305 OPEN/CLOSE COMMAND | 141-MFD-0305-ZIO | MOTORIZED GAS DAMPER 141-MFD-0305 OPEN FEEDBACK
141-MFD-0 | 305 | 141-MFD-0305 |  |  | 141-MFD-0305-ZIC | MOTORIZED GAS DAMPER 141-MFD-0305 CLOSE FEEDBACK
141-MFD-0 | 306 | 141-MFD-0306 | 141-MFD-0306-CMD | MOTORIZED FIRE DAMPER 141-MFD-0306 OPEN/CLOSE COMMAND | 141-MFD-0306-ZIO | MOTORIZED GAS DAMPER 141-MFD-0306 OPEN FEEDBACK
141-MFD-0 | 306 | 141-MFD-0306 |  |  | 141-MFD-0306-ZIC | MOTORIZED GAS DAMPER 141-MFD-0306 CLOSE FEEDBACK
141-MFD-0 | 307 | 141-MFD-0307 | 141-MFD-0307-CMD | MOTORIZED FIRE DAMPER 141-MFD-0307 OPEN/CLOSE COMMAND | 141-MFD-0307-ZIO | MOTORIZED GAS DAMPER 141-MFD-0307 OPEN FEEDBACK
141-MFD-0 | 307 | 141-MFD-0307 |  |  | 141-MFD-0307-ZIC | MOTORIZED GAS DAMPER 141-MFD-0307 CLOSE FEEDBACK
141-MFD-0 | 308 | 141-MFD-0308 | 141-MFD-0308-CMD | MOTORIZED FIRE DAMPER 141-MFD-0308 OPEN/CLOSE COMMAND | 141-MFD-0308-ZIO | MOTORIZED GAS DAMPER 141-MFD-0308 OPEN FEEDBACK
141-MFD-0 | 308 | 141-MFD-0308 |  |  | 141-MFD-0308-ZIC | MOTORIZED GAS DAMPER 141-MFD-0308 CLOSE FEEDBACK
141-MFD-0 | 309 | 141-MFD-0309 | 141-MFD-0309-CMD | MOTORIZED FIRE DAMPER 141-MFD-0309 OPEN/CLOSE COMMAND | 141-MFD-0309-ZIO | MOTORIZED GAS DAMPER 141-MFD-0309 OPEN FEEDBACK
141-MFD-0 | 309 | 141-MFD-0309 |  |  | 141-MFD-0309-ZIC | MOTORIZED GAS DAMPER 141-MFD-0309 CLOSE FEEDBACK
141-MFD-0 | 310 | 141-MFD-0310 | 141-MFD-0310-CMD | MOTORIZED FIRE DAMPER 141-MFD-0310 OPEN/CLOSE COMMAND | 141-MFD-0310-ZIO | MOTORIZED GAS DAMPER 141-MFD-0310 OPEN FEEDBACK
141-MFD-0 | 310 | 141-MFD-0310 |  |  | 141-MFD-0310-ZIC | MOTORIZED GAS DAMPER 141-MFD-0310 CLOSE FEEDBACK
141-MFD-0 | 311 | 141-MFD-0311 | 141-MFD-0311-CMD | MOTORIZED FIRE DAMPER 141-MFD-0311 OPEN/CLOSE COMMAND | 141-MFD-0311-ZIO | MOTORIZED GAS DAMPER 141-MFD-0311 OPEN FEEDBACK
141-MFD-0 | 311 | 141-MFD-0311 |  |  | 141-MFD-0311-ZIC | MOTORIZED GAS DAMPER 141-MFD-0311 CLOSE FEEDBACK
141-MFD-0 | 312 | 141-MFD-0312 | 141-MFD-0312-CMD | MOTORIZED FIRE DAMPER 141-MFD-0312 OPEN/CLOSE COMMAND | 141-MFD-0312-ZIO | MOTORIZED GAS DAMPER 141-MFD-0312 OPEN FEEDBACK
141-MFD-0 | 312 | 141-MFD-0312 |  |  | 141-MFD-0312-ZIC | MOTORIZED GAS DAMPER 141-MFD-0312 CLOSE FEEDBACK
141-MFD-0 | 313 | 141-MFD-0313 | 141-MFD-0313-CMD | MOTORIZED FIRE DAMPER 141-MFD-0313 OPEN/CLOSE COMMAND | 141-MFD-0313-ZIO | MOTORIZED GAS DAMPER 141-MFD-0313 OPEN FEEDBACK
141-MFD-0 | 313 | 141-MFD-0313 |  |  | 141-MFD-0313-ZIC | MOTORIZED GAS DAMPER 141-MFD-0313 CLOSE FEEDBACK
141-MFD-0 | 314 | 141-MFD-0314 | 141-MFD-0314-CMD | MOTORIZED FIRE DAMPER 141-MFD-0314 OPEN/CLOSE COMMAND | 141-MFD-0314-ZIO | MOTORIZED GAS DAMPER 141-MFD-0314 OPEN FEEDBACK
141-MFD-0 | 314 | 141-MFD-0314 |  |  | 141-MFD-0314-ZIC | MOTORIZED GAS DAMPER 141-MFD-0314 CLOSE FEEDBACK
141-MFD-0 | 315 | 141-MFD-0315 | 141-MFD-0315-CMD | MOTORIZED FIRE DAMPER 141-MFD-0315 OPEN/CLOSE COMMAND | 141-MFD-0315-ZIO | MOTORIZED GAS DAMPER 141-MFD-0315 OPEN FEEDBACK
141-MFD-0 | 315 | 141-MFD-0315 |  |  | 141-MFD-0315-ZIC | MOTORIZED GAS DAMPER 141-MFD-0315 CLOSE FEEDBACK
141-MFD-0 | 316 | 141-MFD-0316 | 141-MFD-0316-CMD | MOTORIZED FIRE DAMPER 141-MFD-0316 OPEN/CLOSE COMMAND | 141-MFD-0316-ZIO | MOTORIZED GAS DAMPER 141-MFD-0316 OPEN FEEDBACK
141-MFD-0 | 316 | 141-MFD-0316 |  |  | 141-MFD-0316-ZIC | MOTORIZED GAS DAMPER 141-MFD-0316 CLOSE FEEDBACK
141-MFD-0 | 317 | 141-MFD-0317 | 141-MFD-0317-CMD | MOTORIZED FIRE DAMPER 141-MFD-0317 OPEN/CLOSE COMMAND | 141-MFD-0317-ZIO | MOTORIZED GAS DAMPER 141-MFD-0317 OPEN FEEDBACK
141-MFD-0 | 317 | 141-MFD-0317 |  |  | 141-MFD-0317-ZIC | MOTORIZED GAS DAMPER 141-MFD-0317 CLOSE FEEDBACK
141-MFD-0 | 318 | 141-MFD-0318 | 141-MFD-0318-CMD | MOTORIZED FIRE DAMPER 141-MFD-0318 OPEN/CLOSE COMMAND | 141-MFD-0318-ZIO | MOTORIZED GAS DAMPER 141-MFD-0318 OPEN FEEDBACK
141-MFD-0 | 318 | 141-MFD-0318 |  |  | 141-MFD-0318-ZIC | MOTORIZED GAS DAMPER 141-MFD-0318 CLOSE FEEDBACK
141-MFD-0 | 319 | 141-MFD-0319 | 141-MFD-0319-CMD | MOTORIZED FIRE DAMPER 141-MFD-0319 OPEN/CLOSE COMMAND | 141-MFD-0319-ZIO | MOTORIZED GAS DAMPER 141-MFD-0319 OPEN FEEDBACK
141-MFD-0 | 319 | 141-MFD-0319 |  |  | 141-MFD-0319-ZIC | MOTORIZED GAS DAMPER 141-MFD-0319 CLOSE FEEDBACK
141-MFD-0 | 320 | 141-MFD-0320 | 141-MFD-0320-CMD | MOTORIZED FIRE DAMPER 141-MFD-0320 OPEN/CLOSE COMMAND | 141-MFD-0320-ZIO | MOTORIZED GAS DAMPER 141-MFD-0320 OPEN FEEDBACK
141-MFD-0 | 320 | 141-MFD-0320 |  |  | 141-MFD-0320-ZIC | MOTORIZED GAS DAMPER 141-MFD-0320 CLOSE FEEDBACK
141-MFD-0 | 321 | 141-MFD-0321 | 141-MFD-0321-CMD | MOTORIZED FIRE DAMPER 141-MFD-0321 OPEN/CLOSE COMMAND | 141-MFD-0321-ZIO | MOTORIZED GAS DAMPER 141-MFD-0321 OPEN FEEDBACK
141-MFD-0 | 321 | 141-MFD-0321 |  |  | 141-MFD-0321-ZIC | MOTORIZED GAS DAMPER 141-MFD-0321 CLOSE FEEDBACK
141-MFD-0 | 322 | 141-MFD-0322 | 141-MFD-0322-CMD | MOTORIZED FIRE DAMPER 141-MFD-0322 OPEN/CLOSE COMMAND | 141-MFD-0322-ZIO | MOTORIZED GAS DAMPER 141-MFD-0322 OPEN FEEDBACK
141-MFD-0 | 322 | 141-MFD-0322 |  |  | 141-MFD-0322-ZIC | MOTORIZED GAS DAMPER 141-MFD-0322 CLOSE FEEDBACK
141-MFD-0 | 323 | 141-MFD-0323 | 141-MFD-0323-CMD | MOTORIZED FIRE DAMPER 141-MFD-0323 OPEN/CLOSE COMMAND | 141-MFD-0323-ZIO | MOTORIZED GAS DAMPER 141-MFD-0323 OPEN FEEDBACK
141-MFD-0 | 323 | 141-MFD-0323 |  |  | 141-MFD-0323-ZIC | MOTORIZED GAS DAMPER 141-MFD-0323 CLOSE FEEDBACK
141-MFD-0 | 324 | 141-MFD-0324 | 141-MFD-0324-CMD | MOTORIZED FIRE DAMPER 141-MFD-0324 OPEN/CLOSE COMMAND | 141-MFD-0324-ZIO | MOTORIZED GAS DAMPER 141-MFD-0324 OPEN FEEDBACK
141-MFD-0 | 324 | 141-MFD-0324 |  |  | 141-MFD-0324-ZIC | MOTORIZED GAS DAMPER 141-MFD-0324 CLOSE FEEDBACK
141-MFD-0 | 325 | 141-MFD-0325 | 141-MFD-0325-CMD | MOTORIZED FIRE DAMPER 141-MFD-0325 OPEN/CLOSE COMMAND | 141-MFD-0325-ZIO | MOTORIZED GAS DAMPER 141-MFD-0325 OPEN FEEDBACK
141-MFD-0 | 325 | 141-MFD-0325 |  |  | 141-MFD-0325-ZIC | MOTORIZED GAS DAMPER 141-MFD-0325 CLOSE FEEDBACK
141-MFD-0 | 326 | 141-MFD-0326 | 141-MFD-0326-CMD | MOTORIZED FIRE DAMPER 141-MFD-0326 OPEN/CLOSE COMMAND | 141-MFD-0326-ZIO | MOTORIZED GAS DAMPER 141-MFD-0326 OPEN FEEDBACK
141-MFD-0 | 326 | 141-MFD-0326 |  |  | 141-MFD-0326-ZIC | MOTORIZED GAS DAMPER 141-MFD-0326 CLOSE FEEDBACK
141-GD-0 | 331 | 141-GD-0331 | 141-GD-0331-CMD | MOTORIZED FIRE DAMPER 141-GD-0331 OPEN/CLOSE COMMAND
141-GD-0 | 332 | 141-GD-0332 | 141-GD-0332-CMD | MOTORIZED FIRE DAMPER 141-GD-0332 OPEN/CLOSE COMMAND
141-GD-0 | 333 | 141-GD-0333 | 141-GD-0333-CMD | MOTORIZED FIRE DAMPER 141-GD-0333 OPEN/CLOSE COMMAND
141-GD-0 | 334 | 141-GD-0334 | 141-GD-0334-CMD | MOTORIZED FIRE DAMPER 141-GD-0334 OPEN/CLOSE COMMAND
141-GD-0 | 336 | 141-GD-0336 | 141-GD-0336-CMD | MOTORIZED FIRE DAMPER 141-GD-0336 OPEN/CLOSE COMMAND
141-GD-0
141-GD-0
141-GD-0
141-GD-0
141-GD-0
141-GD-0
141-GD-0
141-GD-0
141-GD-0
141-GD-0

## Sheet2 (hidden)
MOTORIZED GAS DAMPER 141-GD-0103 OPEN STATUS
MOTORIZED GAS DAMPER 141-GD-0103 CLOSE STATUS
| 141-GD-0302 | OPEN STATUS | ZIO | 141-GD-0302-ZIO | MOTORIZED GAS DAMPER 141-GD-0302 OPEN STATUS
| 141-GD-0302 | CLOSE STATUS | ZIC | 141-GD-0302-ZIC | MOTORIZED GAS DAMPER 141-GD-0302 CLOSE STATUS
| 141-GD-0303 | OPEN STATUS | ZIO | 141-GD-0303-ZIO | MOTORIZED GAS DAMPER 141-GD-0303 OPEN STATUS
| 141-GD-0303 | CLOSE STATUS | ZIC | 141-GD-0303-ZIC | MOTORIZED GAS DAMPER 141-GD-0303 CLOSE STATUS
| 141-GD-0304 | OPEN STATUS | ZIO | 141-GD-0304-ZIO | MOTORIZED GAS DAMPER 141-GD-0304 OPEN STATUS
| 141-GD-0304 | CLOSE STATUS | ZIC | 141-GD-0304-ZIC | MOTORIZED GAS DAMPER 141-GD-0304 CLOSE STATUS
| 141-GD-0305 | OPEN STATUS | ZIO | 141-GD-0305-ZIO | MOTORIZED GAS DAMPER 141-GD-0305 OPEN STATUS
| 141-GD-0305 | CLOSE STATUS | ZIC | 141-GD-0305-ZIC | MOTORIZED GAS DAMPER 141-GD-0305 CLOSE STATUS
| 141-GD-0306 | OPEN STATUS | ZIO | 141-GD-0306-ZIO | MOTORIZED GAS DAMPER 141-GD-0306 OPEN STATUS
| 141-GD-0306 | CLOSE STATUS | ZIC | 141-GD-0306-ZIC | MOTORIZED GAS DAMPER 141-GD-0306 CLOSE STATUS
| 141-GD-0307 | OPEN STATUS | ZIO | 141-GD-0307-ZIO | MOTORIZED GAS DAMPER 141-GD-0307 OPEN STATUS
| 141-GD-0307 | CLOSE STATUS | ZIC | 141-GD-0307-ZIC | MOTORIZED GAS DAMPER 141-GD-0307 CLOSE STATUS
| 141-GD-0308 | OPEN STATUS | ZIO | 141-GD-0308-ZIO | MOTORIZED GAS DAMPER 141-GD-0308 OPEN STATUS
| 141-GD-0308 | CLOSE STATUS | ZIC | 141-GD-0308-ZIC | MOTORIZED GAS DAMPER 141-GD-0308 CLOSE STATUS
| 141-GD-0309 | OPEN STATUS | ZIO | 141-GD-0309-ZIO | MOTORIZED GAS DAMPER 141-GD-0309 OPEN STATUS
| 141-GD-0309 | CLOSE STATUS | ZIC | 141-GD-0309-ZIC | MOTORIZED GAS DAMPER 141-GD-0309 CLOSE STATUS
| 141-GD-0310 | OPEN STATUS | ZIO | 141-GD-0310-ZIO | MOTORIZED GAS DAMPER 141-GD-0310 OPEN STATUS
| 141-GD-0310 | CLOSE STATUS | ZIC | 141-GD-0310-ZIC | MOTORIZED GAS DAMPER 141-GD-0310 CLOSE STATUS
| 141-GD-0311 | OPEN STATUS | ZIO | 141-GD-0311-ZIO | MOTORIZED GAS DAMPER 141-GD-0311 OPEN STATUS
| 141-GD-0311 | CLOSE STATUS | ZIC | 141-GD-0311-ZIC | MOTORIZED GAS DAMPER 141-GD-0311 CLOSE STATUS
| 141-GD-0312 | OPEN STATUS | ZIO | 141-GD-0312-ZIO | MOTORIZED GAS DAMPER 141-GD-0312 OPEN STATUS
| 141-GD-0312 | CLOSE STATUS | ZIC | 141-GD-0312-ZIC | MOTORIZED GAS DAMPER 141-GD-0312 CLOSE STATUS
| 141-GD-0313 | OPEN STATUS | ZIO | 141-GD-0313-ZIO | MOTORIZED GAS DAMPER 141-GD-0313 OPEN STATUS
| 141-GD-0313 | CLOSE STATUS | ZIC | 141-GD-0313-ZIC | MOTORIZED GAS DAMPER 141-GD-0313 CLOSE STATUS
| 141-GD-0314 | OPEN STATUS | ZIO | 141-GD-0314-ZIO | MOTORIZED GAS DAMPER 141-GD-0314 OPEN STATUS
| 141-GD-0314 | CLOSE STATUS | ZIC | 141-GD-0314-ZIC | MOTORIZED GAS DAMPER 141-GD-0314 CLOSE STATUS
| 141-GD-0315 | OPEN STATUS | ZIO | 141-GD-0315-ZIO | MOTORIZED GAS DAMPER 141-GD-0315 OPEN STATUS
| 141-GD-0315 | CLOSE STATUS | ZIC | 141-GD-0315-ZIC | MOTORIZED GAS DAMPER 141-GD-0315 CLOSE STATUS
| 141-GD-0316 | OPEN STATUS | ZIO | 141-GD-0316-ZIO | MOTORIZED GAS DAMPER 141-GD-0316 OPEN STATUS
| 141-GD-0316 | CLOSE STATUS | ZIC | 141-GD-0316-ZIC | MOTORIZED GAS DAMPER 141-GD-0316 CLOSE STATUS
| 141-GD-0317 | OPEN STATUS | ZIO | 141-GD-0317-ZIO | MOTORIZED GAS DAMPER 141-GD-0317 OPEN STATUS
| 141-GD-0317 | CLOSE STATUS | ZIC | 141-GD-0317-ZIC | MOTORIZED GAS DAMPER 141-GD-0317 CLOSE STATUS
| 141-GD-0318 | OPEN STATUS | ZIO | 141-GD-0318-ZIO | MOTORIZED GAS DAMPER 141-GD-0318 OPEN STATUS
| 141-GD-0318 | CLOSE STATUS | ZIC | 141-GD-0318-ZIC | MOTORIZED GAS DAMPER 141-GD-0318 CLOSE STATUS
| 141-GD-0320 | OPEN STATUS | ZIO | 141-GD-0320-ZIO | MOTORIZED GAS DAMPER 141-GD-0320 OPEN STATUS
| 141-GD-0320 | CLOSE STATUS | ZIC | 141-GD-0320-ZIC | MOTORIZED GAS DAMPER 141-GD-0320 CLOSE STATUS
| 141-GD-0321 | OPEN STATUS | ZIO | 141-GD-0321-ZIO | MOTORIZED GAS DAMPER 141-GD-0321 OPEN STATUS
| 141-GD-0321 | CLOSE STATUS | ZIC | 141-GD-0321-ZIC | MOTORIZED GAS DAMPER 141-GD-0321 CLOSE STATUS
| 141-GD-0322 | OPEN STATUS | ZIO | 141-GD-0322-ZIO | MOTORIZED GAS DAMPER 141-GD-0322 OPEN STATUS
| 141-GD-0322 | CLOSE STATUS | ZIC | 141-GD-0322-ZIC | MOTORIZED GAS DAMPER 141-GD-0322 CLOSE STATUS
| 141-GD-0324 | OPEN STATUS | ZIO | 141-GD-0324-ZIO | MOTORIZED GAS DAMPER 141-GD-0324 OPEN STATUS
| 141-GD-0324 | CLOSE STATUS | ZIC | 141-GD-0324-ZIC | MOTORIZED GAS DAMPER 141-GD-0324 CLOSE STATUS
| 141-GD-0325 | OPEN STATUS | ZIO | 141-GD-0325-ZIO | MOTORIZED GAS DAMPER 141-GD-0325 OPEN STATUS
| 141-GD-0325 | CLOSE STATUS | ZIC | 141-GD-0325-ZIC | MOTORIZED GAS DAMPER 141-GD-0325 CLOSE STATUS
| 141-GD-0326 | OPEN STATUS | ZIO | 141-GD-0326-ZIO | MOTORIZED GAS DAMPER 141-GD-0326 OPEN STATUS
| 141-GD-0326 | CLOSE STATUS | ZIC | 141-GD-0326-ZIC | MOTORIZED GAS DAMPER 141-GD-0326 CLOSE STATUS
| 141-GD-0331 | OPEN STATUS | ZIO | 141-GD-0331-ZIO | MOTORIZED GAS DAMPER 141-GD-0331 OPEN STATUS
| 141-GD-0331 | CLOSE STATUS | ZIC | 141-GD-0331-ZIC | MOTORIZED GAS DAMPER 141-GD-0331 CLOSE STATUS
| 141-GD-0332 | OPEN STATUS | ZIO | 141-GD-0332-ZIO | MOTORIZED GAS DAMPER 141-GD-0332 OPEN STATUS
| 141-GD-0332 | CLOSE STATUS | ZIC | 141-GD-0332-ZIC | MOTORIZED GAS DAMPER 141-GD-0332 CLOSE STATUS
| 141-GD-0333 | OPEN STATUS | ZIO | 141-GD-0333-ZIO | MOTORIZED GAS DAMPER 141-GD-0333 OPEN STATUS
| 141-GD-0333 | CLOSE STATUS | ZIC | 141-GD-0333-ZIC | MOTORIZED GAS DAMPER 141-GD-0333 CLOSE STATUS
| 141-GD-0334 | OPEN STATUS | ZIO | 141-GD-0334-ZIO | MOTORIZED GAS DAMPER 141-GD-0334 OPEN STATUS
| 141-GD-0334 | CLOSE STATUS | ZIC | 141-GD-0334-ZIC | MOTORIZED GAS DAMPER 141-GD-0334 CLOSE STATUS
| 141-GD-0336 | OPEN STATUS | ZIO | 141-GD-0336-ZIO | MOTORIZED GAS DAMPER 141-GD-0336 OPEN STATUS
| 141-GD-0336 | CLOSE STATUS | ZIC | 141-GD-0336-ZIC | MOTORIZED GAS DAMPER 141-GD-0336 CLOSE STATUS

## Sheet3 (hidden)
Sl No | Comment Ref | Comments | Response
1 | Page 1 of 7 | General Comment: 1. All Interface signals shall be covered under separate section for ease of identification and subsequent consideration to 3rd party system ( eg. LFCP, DCS) 2. Interface Signal list (including soft signals) shall be in line with all signals shown in HVAC P&ID /HVAC Design basis. 3. As per HVAC P&ID /HVAC Design basis, there is a MODBUS TCP/IP connectivity between HVAC PLC and DCS for monitoring of HVAC related signals including equipment status; accordingly all applicable signals shall be populated in this IO list. 4. Also, this IO list shall be updated in line with Building F&G cause and effect matrix for the applicable signals to HVAC system. 5. UPS Voltage is 240 VAC and not 230VAC | 1. Refer column "FROM/TO" for source details, it is already grouped based on sources in each IO type. 2. Complied, 3. All Modbus signals will be part of spearate deliverable for Modbus mapping list. 4. Complied, same is shown in System Architecture, 5. Noted and Updated, 6. Noted and Updated
2 | Page 3 of 7 | Building F&G control panel acronym for this project is: LFCP (Local Fire Control Panel) | Noted and Updated
3 | Page 3 of 7 | LFCP(F&G) outputs are normally dry contacts. Here 'sink' input type would mean PLC expects LFCP to act as power source. Vendor to confirm whether Sink refers to the connected device or change type to Source; otherwise the final selection is subject to review meeting. | Dry input considered, 24VDC from HVAC PLC panel will flow through the dry contact.
4 | Page 3 of 7 | AND ALL DAMPERS CLOSE, AND AIR INTAKE DAMPER CLOSE | Noted and Updated
5 | Page 5 of 7 | Vendor to confirm VF stands for voltage free contacts exposed to LFCP (F&G) as DO. | Confirmed
6 | Page 5 of 7 | LFCP TAG: will follow | Noted and Confirmed
7 | Page 6 of 7 | Check the terminals. May analog inputs are addressed at the same terminals. | Noted and Updated