## DI
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
SUBSTATION-02
RUWAIS - U.A.E.
[10 empty] | FACILITY NAME: BOROUGE 4 |  |  |  | COMPANY PROJ. NO. |  | 4700000897
[14 empty] | CONTRACTOR. PROJ. NO. |  | 083118C
|  | SS-02-HVAC-CP | [7 empty] | DOCUMENT TITLE: SS-02 HVAC PLC System - I/O List |  |  |  | SUBCONTR. ID |  | -
Sl. No. | IM Module | I/O Detail |  |  |  |  | FROM | EQUIPMENT TAG | PLC TAG | Description | States |  | PLC Term. | TB GROUP |  | Verified & Signed (Remarks)
|  | Module | Supply | Type | Range | Unit |  |  |  |  | FALSE | TRUE
DIGITAL INPUT
1 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 141-GC-0105A | CHLR1_RUN | CHILLER-1 UNIT RUN STATUS | STOPPED | RUNNING | I0.0 | XDI1-1 | XDI1-2
2 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 141-GC-0105A | CHLR1_TRP | CHILLER-1 UNIT TRIP STATUS | NORMAL | TRIP | I0.1 | XDI1-3 | XDI1-4
3 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 141-GC-0105A | CHLR1_RMT | CHILLER-1 REMOTE MODE STATUS | LOCAL | REMOTE | I0.2 | XDI1-5 | XDI1-6
4 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-205B | 141-GC-0105A | CHLR1_BRK_TRP | CHILLER-1 UNIT BREAKER TRIP STATUS | NORMAL | TRIP | I0.3 | XDI1-7 | XDI1-8
5 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 141-GC-0105A | CHLR1_FS | CHILLER-1 FLOW SWITCH STATUS | NO FLOW | FLOW ON | I0.4 | XDI1-9 | XDI1-10
6 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-205B | 141-GA-0105A | AHU1_FAN1_RUN | AHU-1 FAN-1 RUN STATUS | STOPPED | RUNNING | I0.5 | XDI1-11 | XDI1-12
7 | IM1 | DI1 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I0.6 | XDI1-13 | XDI1-14
8 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-205B | 141-GA-0105A | AHU1_FAN1_RMT | AHU-1 FAN-1 REMOTE MODE STATUS | LOCAL | REMOTE | I0.7 | XDI1-15 | XDI1-16
9 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-205B | 141-GA-0105A | AHU1_FAN1_BRK_TRP | AHU-1 FAN-1 UNIT BREAKER TRIP STATUS | NORMAL | TRIP | I1.0 | XDI1-17 | XDI1-18
10 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 141-GA-0105A | AHU1_PF_DPS | AHU-1 PRE-FILTER DIFFERENTIAL PRESSURE HIGH | NORMAL | ALARM | I1.1 | XDI1-19 | XDI1-20
11 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 141-GA-0105A | AHU1_FF_DPS | AHU-1 FINE-FILTER DIFFERENTIAL PRESSURE HIGH | NORMAL | ALARM | I1.2 | XDI1-21 | XDI1-22
12 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 141-GA-0105A | AHU1_AF_DPS | AHU-1 FAN AIR FLOW DIFFERENTIAL PRESSURE | NO FLOW | FLOW ON | I1.3 | XDI1-23 | XDI1-24
13 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-205B | 141-GK-0103A | BAT_FAN1_RUN | BATTERY ROOM FAN-1 RUN STATUS | STOPPED | RUNNING | I1.4 | XDI1-25 | XDI1-26
14 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-205B | 141-GK-0103A | BAT_FAN1_TRP | BATTERY ROOM FAN-1 TRIP STATUS | NORMAL | TRIP | I1.5 | XDI1-27 | XDI1-28
15 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-205B | 141-GK-0103A | BAT_FAN1_RMT | BATTERY ROOM FAN-1 REMOTE MODE STATUS | LOCAL | REMOTE | I1.6 | XDI1-29 | XDI1-30
16 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-205B | 141-GK-0103A | BAT_FAN1_ES | BATTERY ROOM FAN-1 EMERGENCY STOP | NORMAL | ACTIVE | I1.7 | XDI1-31 | XDI1-32
17 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 141-GK-0103A | BAT_FAN1_DPS | DIFFERENTIAL PRESSURE ACROSS BATTERY ROOM FAN-1 | NO FLOW | FLOW ON | I2.0 | XDI2-1 | XDI2-2
18 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-205B | 141-PC-0105A | CHLR1_PMP_RUN | CHILLER-1 WATER PUMP RUN STATUS | STOPPED | RUNNING | I2.1 | XDI2-3 | XDI2-4
19 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-205B | 141-PC-0105A | CHLR1_PMP_TRP | CHILLER-1 WATER PUMP TRIP STATUS | NORMAL | TRIP | I2.2 | XDI2-5 | XDI2-6
20 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-205B | 141-PC-0105A | CHLR1_PMP_RMT | CHILLER-1 WATER PUMP REMOTE MODE STATUS | LOCAL | REMOTE | I2.3 | XDI2-7 | XDI2-8
21 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-205B | 141-PC-0105A | CHLR1_PMP_ES | CHILLER-1 WATER PUMP EMERGENCY STOP | NORMAL | ACTIVE | I2.4 | XDI2-9 | XDI2-10
22 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-205B | - | BLD_FAN_RUN | BLEED FAN RUN STATUS | STOPPED | RUNNING | I2.5 | XDI2-11 | XDI2-12
23 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-205B | - | BLD_FAN_TRP | BLEED FAN TRIP STATUS | NORMAL | TRIP | I2.6 | XDI2-13 | XDI2-14
24 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-205B | - | BLD_FAN_RMT | BLEED FAN REMOTE MODE STATUS | LOCAL | REMOTE | I2.7 | XDI2-15 | XDI2-16
25 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-205B | - | BLD_FAN_ES | BLEED FAN EMERGENCY STOP | NORMAL | ACTIVE | I3.0 | XDI2-17 | XDI2-18
26 | IM1 | DI2 | 24VDC | VF | - | - | FIELD | - | AHU1-BFV-ZIO | MOTORIZED BUTTER FLY VALVE AHU-1 OPEN STATUS | NOT OPEN | OPEN | I3.1 | XDI2-19 | XDI2-20
27 | IM1 | DI2 | 24VDC | VF | - | - | FIELD | - | AHU1-BFV-ZIC | MOTORIZED BUTTER FLY VALVE AHU-1 CLOSE STATUS | NOT CLOSE | CLOSE | I3.2 | XDI2-21 | XDI2-22
28 | IM1 | DI2 | 24VDC | VF | - | - | FIELD | 141-GD-0221 | 141-GD-0221-ZIO | MOTORIZED SHUTOFF DAMPER 141-GD-0221 OPEN STATUS | NOT OPEN | OPEN | I3.3 | XDI2-23 | XDI2-24
29 | IM1 | DI2 | 24VDC | VF | - | - | FIELD | 141-GD-0221 | 141-GD-0221-ZIC | MOTORIZED SHUTOFF DAMPER 141-GD-0221 CLOSE STATUS | NOT CLOSE | CLOSE | I3.4 | XDI2-25 | XDI2-26
30 | IM1 | DI2 | 24VDC | VF | - | - | FIELD | 141-GD-0223 | 141-GD-0223-ZIO | MOTORIZED SHUTOFF DAMPER 141-GD-0223 OPEN STATUS | NOT OPEN | OPEN | I3.5 | XDI2-27 | XDI2-28
31 | IM1 | DI2 | 24VDC | VF | - | - | FIELD | 141-GD-0223 | 141-GD-0223-ZIC | MOTORIZED SHUTOFF DAMPER 141-GD-0223 CLOSE STATUS | NOT CLOSE | CLOSE | I3.6 | XDI2-29 | XDI2-30
32 | IM1 | DI2 | 24VDC | VF | - | - | FIELD | 141-GD-0226 | 141-GD-0226-ZIO | MOTORIZED SHUTOFF DAMPER 141-GD-0226 OPEN STATUS | NOT OPEN | OPEN | I3.7 | XDI2-31 | XDI2-32
33 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0226 | 141-GD-0226-ZIC | MOTORIZED SHUTOFF DAMPER 141-GD-0226 CLOSE STATUS | NOT CLOSE | CLOSE | I4.0 | XDI3-1 | XDI3-2
34 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0201 | 141-GD-0201-ZIO | MOTORIZED GAS DAMPER 141-GD-0201 OPEN STATUS | NOT OPEN | OPEN | I4.1 | XDI3-3 | XDI3-4
35 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0201 | 141-GD-0201-ZIC | MOTORIZED GAS DAMPER 141-GD-0201 CLOSE STATUS | NOT CLOSE | CLOSE | I4.2 | XDI3-5 | XDI3-6
36 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0202 | 141-GD-0202-ZIO | MOTORIZED FIRE DAMPER 141-GD-0202 OPEN STATUS | NOT OPEN | OPEN | I4.3 | XDI3-7 | XDI3-8
37 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0202 | 141-GD-0202-ZIC | MOTORIZED FIRE DAMPER 141-GD-0202 CLOSE STATUS | NOT CLOSE | CLOSE | I4.4 | XDI3-9 | XDI3-10
38 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0203 | 141-GD-0203-ZIO | MOTORIZED FIRE DAMPER 141-GD-0203 OPEN STATUS | NOT OPEN | OPEN | I4.5 | XDI3-11 | XDI3-12
39 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0203 | 141-GD-0203-ZIC | MOTORIZED FIRE DAMPER 141-GD-0203 CLOSE STATUS | NOT CLOSE | CLOSE | I4.6 | XDI3-13 | XDI3-14
40 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0204 | 141-GD-0204-ZIO | MOTORIZED FIRE DAMPER 141-GD-0204 OPEN STATUS | NOT OPEN | OPEN | I4.7 | XDI3-15 | XDI3-16
41 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0204 | 141-GD-0204-ZIC | MOTORIZED FIRE DAMPER 141-GD-0204 CLOSE STATUS | NOT CLOSE | CLOSE | I5.0 | XDI3-17 | XDI3-18
42 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0205 | 141-GD-0205-ZIO | MOTORIZED FIRE DAMPER 141-GD-0205 OPEN STATUS | NOT OPEN | OPEN | I5.1 | XDI3-19 | XDI3-20
43 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0205 | 141-GD-0205-ZIC | MOTORIZED FIRE DAMPER 141-GD-0205 CLOSE STATUS | NOT CLOSE | CLOSE | I5.2 | XDI3-21 | XDI3-22
44 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0206 | 141-GD-0206-ZIO | MOTORIZED FIRE DAMPER 141-GD-0206 OPEN STATUS | NOT OPEN | OPEN | I5.3 | XDI3-23 | XDI3-24
45 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0206 | 141-GD-0206-ZIC | MOTORIZED FIRE DAMPER 141-GD-0206 CLOSE STATUS | NOT CLOSE | CLOSE | I5.4 | XDI3-25 | XDI3-26
46 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0207 | 141-GD-0207-ZIO | MOTORIZED FIRE DAMPER 141-GD-0207 OPEN STATUS | NOT OPEN | OPEN | I5.5 | XDI3-27 | XDI3-28
47 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0207 | 141-GD-0207-ZIC | MOTORIZED FIRE DAMPER 141-GD-0207 CLOSE STATUS | NOT CLOSE | CLOSE | I5.6 | XDI3-29 | XDI3-30
48 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0208 | 141-GD-0208-ZIO | MOTORIZED FIRE DAMPER 141-GD-0208 OPEN STATUS | NOT OPEN | OPEN | I5.7 | XDI3-31 | XDI3-32
49 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0208 | 141-GD-0208-ZIC | MOTORIZED FIRE DAMPER 141-GD-0208 CLOSE STATUS | NOT CLOSE | CLOSE | I6.0 | XDI4-1 | XDI4-2
50 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0209 | 141-GD-0209-ZIO | MOTORIZED FIRE DAMPER 141-GD-0209 OPEN STATUS | NOT OPEN | OPEN | I6.1 | XDI4-3 | XDI4-4
51 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0209 | 141-GD-0209-ZIC | MOTORIZED FIRE DAMPER 141-GD-0209 CLOSE STATUS | NOT CLOSE | CLOSE | I6.2 | XDI4-5 | XDI4-6
52 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0210 | 141-GD-0210-ZIO | MOTORIZED FIRE DAMPER 141-GD-0210 OPEN STATUS | NOT OPEN | OPEN | I6.3 | XDI4-7 | XDI4-8
53 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0210 | 141-GD-0210-ZIC | MOTORIZED FIRE DAMPER 141-GD-0210 CLOSE STATUS | NOT CLOSE | CLOSE | I6.4 | XDI4-9 | XDI4-10
54 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0211 | 141-GD-0211-ZIO | MOTORIZED FIRE DAMPER 141-GD-0211 OPEN STATUS | NOT OPEN | OPEN | I6.5 | XDI4-11 | XDI4-12
55 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0211 | 141-GD-0211-ZIC | MOTORIZED FIRE DAMPER 141-GD-0211 CLOSE STATUS | NOT CLOSE | CLOSE | I6.6 | XDI4-13 | XDI4-14
56 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GB-0118 | SWG_HTR_TRP | LVSWITCHGEAR ROOM ROOM HEATER TRIP STATUS | NORMAL | TRIP | I6.7 | XDI4-15 | XDI4-16
57 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GB-0118 | SWG_HTR_ON | LVSWITCHGEAR HEATER ON/OFF STATUS | OFF | ON | I7.0 | XDI4-17 | XDI4-18
58 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GB-0114 | RR_HTR_TRP | RACK ROOM HEATER TRIP STATUS | NORMAL | TRIP | I7.1 | XDI4-19 | XDI4-20
59 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GB-0114 | RR_HTR_ON | RACK ROOM HEATER ON/OFF STATUS | OFF | ON | I7.2 | XDI4-21 | XDI4-22
60 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GB-0115 | BAT_HTR_TRP | BATTERY ROOM HEATER TRIP STATUS | NORMAL | TRIP | I7.3 | XDI4-23 | XDI4-24
61 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GB-0115 | BAT_HTR_ON | BATTERYROOM HEATER ON/OFF STATUS | OFF | ON | I7.4 | XDI4-25 | XDI4-26
62 | IM1 | DI4 | 24VDC | VF | - | - | 141-ES-205A | - | EMG_STP | HVACP EMERGENCY STOP | NORMAL | ACTIVE | I7.5 | XDI4-27 | XDI4-28
63 | IM1 | DI4 | 24VDC | VF | - | - | 141-ES-205A | - | MUTE_PB | MUTE PUSH BUTTON | OFF | ON | I7.6 | XDI4-29 | XDI4-30
64 | IM1 | DI4 | 24VDC | VF | - | - | 141-ES-205A | - | RST_PB | RESET PUSH BUTTON | OFF | ON | I7.7 | XDI4-31 | XDI4-32
65 | IM1 | DI5 | 24VDC | VF | - | - | 141-ES-205A | - | PSU1&2_HLTHY | POWER SUPPLY 1 & 2 HEALTHY | UNHEALTHY | HEALTHY | I8.0 | XDI5-1 | XDI5-2
66 | IM1 | DI5 | 24VDC | VF | - | - | 141-ES-205A | - | AFS_HLTHY | PANEL AIR FLOW SWITCH HEALTHY | UNHEALTHY | HEALTHY | I8.1 | XDI5-3 | XDI5-4
67 | IM1 | DI5 | 24VDC | VF | - | - | 141-ES-205A | 141-GA-0105A | AHU1_FAN2_RUN | AHU-1 FAN-2 RUN STATUS | STOPPED | RUNNING | I8.2 | XDI5-5 | XDI5-6
68 | IM1 | DI5 | 24VDC | VF | - | - | 141-ES-205A | 141-GA-0105A | AHU1_FAN2_RMT | AHU-1 FAN-2 REMOTE MODE STATUS | LOCAL | REMOTE | I8.3 | XDI5-7 | XDI5-8
69 | IM1 | DI5 | 24VDC | VF | - | - | 141-ES-205A | 141-GA-0105A | AHU1_FAN2_BRK_TRP | AHU-1 FAN-2 BREAKER TRIP STATUS | NORMAL | TRIP | I8.4 | XDI5-9 | XDI5-10
70 | IM1 | DI5 | 24VDC | VF | - | - | - | - | CHLR1-BFV-ZIO | MOTORIZED BUTTER FLY VALVE CHILLER-1 OPEN STATUS | NOT OPEN | OPEN | I8.5 | XDI5-11 | XDI5-12
71 | IM1 | DI5 | 24VDC | VF | - | - | - | - | CHLR1-BFV-ZIC | MOTORIZED BUTTER FLY VALVE CHILLER-1 CLOSE STATUS | NOT CLOSE | CLOSE | I8.6 | XDI5-13 | XDI5-14
72 | IM1 | DI5 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I8.7 | XDI5-15 | XDI5-16
73 | IM1 | DI5 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I9.0 | XDI5-17 | XDI5-18
74 | IM1 | DI5 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I9.1 | XDI5-19 | XDI5-20
75 | IM1 | DI5 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I9.2 | XDI5-21 | XDI5-22
76 | IM1 | DI5 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I9.3 | XDI5-23 | XDI5-24
77 | IM1 | DI5 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I9.4 | XDI5-25 | XDI5-26
78 | IM1 | DI5 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I9.5 | XDI5-27 | XDI5-28
79 | IM1 | DI5 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I9.6 | XDI5-29 | XDI5-30
80 | IM1 | DI5 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I9.7 | XDI5-31 | XDI5-32
81 | IM2 | DI6 | 24VDC | VF | - | - | FIELD | 141-GC-0105B | CHLR2_RUN | CHILLER-2 UNIT RUN STATUS | STOPPED | RUNNING | I10.0 | XDI6-1 | XDI6-2
82 | IM2 | DI6 | 24VDC | VF | - | - | FIELD | 141-GC-0105B | CHLR2_TRP | CHILLER-2 UNIT TRIP STATUS | NORMAL | TRIP | I10.1 | XDI6-3 | XDI6-4
83 | IM2 | DI6 | 24VDC | VF | - | - | FIELD | 141-GC-0105B | CHLR2_RMT | CHILLER-2 REMOTE MODE STATUS | LOCAL | REMOTE | I10.2 | XDI6-5 | XDI6-6
84 | IM2 | DI6 | 24VDC | VF | - | - | 141-ES-205B | 141-GC-0105B | CHLR2_BRK_TRP | CHILLER-2 UNIT BREAKER TRIP STATUS | NORMAL | TRIP | I10.3 | XDI6-7 | XDI6-8
85 | IM2 | DI6 | 24VDC | VF | - | - | FIELD | 141-GC-0105B | CHLR2_FS | CHILLER-2 FLOW SWITCH STATUS | NO FLOW | FLOW ON | I10.4 | XDI6-9 | XDI6-10
86 | IM2 | DI6 | 24VDC | VF | - | - | 141-ES-205B | 141-GA-0105B | AHU2_RUN | AHU-2 RUN STATUS | STOPPED | RUNNING | I10.5 | XDI6-11 | XDI6-12
87 | IM2 | DI6 | 24VDC | VF | - | - | 141-ES-205B | 141-GA-0105B | AHU2_TRP | AHU-2 TRIP STATUS | NORMAL | TRIP | I10.6 | XDI6-13 | XDI6-14
88 | IM2 | DI6 | 24VDC | VF | - | - | 141-ES-205B | 141-GA-0105B | AHU2_RMT | AHU-2 REMOTE MODE STATUS | LOCAL | REMOTE | I10.7 | XDI6-15 | XDI6-16
89 | IM2 | DI6 | 24VDC | VF | - | - | 141-ES-205B | 141-GA-0105B | AHU2_BRK_TRP | AHU-2 UNIT BREAKER TRIP STATUS | NORMAL | TRIP | I11.0 | XDI6-17 | XDI6-18
90 | IM2 | DI6 | 24VDC | VF | - | - | FIELD | 141-GA-0105B | AHU2_PF_DPS | AHU-2 PRE-FILTER DIFFERENTIAL PRESSURE HIGH | NORMAL | ALARM | I11.1 | XDI6-19 | XDI6-20
91 | IM2 | DI6 | 24VDC | VF | - | - | FIELD | 141-GA-0105B | AHU2_FF_DPS | AHU-2 FINE-FILTER DIFFERENTIAL PRESSURE HIGH | NORMAL | ALARM | I11.2 | XDI6-21 | XDI6-22
92 | IM2 | DI6 | 24VDC | VF | - | - | FIELD | 141-GA-0105B | AHU2_AF_DPS | AHU-2 FAN AIR FLOW DIFFERENTIAL PRESSURE | NO FLOW | FLOW ON | I11.3 | XDI6-23 | XDI6-24
93 | IM2 | DI6 | 24VDC | VF | - | - | 141-ES-205B | 141-GK-0103B | BAT_FAN2_RUN | BATTERY ROOM FAN-2 RUN STATUS | STOPPED | RUNNING | I11.4 | XDI6-25 | XDI6-26
94 | IM2 | DI6 | 24VDC | VF | - | - | 141-ES-205B | 141-GK-0103B | BAT_FAN2_TRP | BATTERY ROOM FAN-2 TRIP STATUS | NORMAL | TRIP | I11.5 | XDI6-27 | XDI6-28
95 | IM2 | DI6 | 24VDC | VF | - | - | 141-ES-205B | 141-GK-0103B | BAT_FAN2_RMT | BATTERY ROOM FAN-2 REMOTE MODE STATUS | LOCAL | REMOTE | I11.6 | XDI6-29 | XDI6-30
96 | IM2 | DI6 | 24VDC | VF | - | - | 141-ES-205B | 141-GK-0103B | BAT_FAN2_ES | BATTERY ROOM FAN-2 EMERGENCY STOP | NORMAL | ACTIVE | I11.7 | XDI6-31 | XDI6-32
97 | IM2 | DI7 | 24VDC | VF | - | - | FIELD | 141-GK-0103B | BAT_FAN2_DPS | DIFFERENTIAL PRESSURE ACROSS BATTERY ROOM FAN-2 | NO FLOW | FLOW ON | I12.0 | XDI7-1 | XDI7-2
98 | IM2 | DI7 | 24VDC | VF | - | - | 141-ES-205B | 141-PC-0105B | CHLR2_PMP_RUN | CHILLER-2 WATER PUMP RUN STATUS | STOPPED | RUNNING | I12.1 | XDI7-3 | XDI7-4
99 | IM2 | DI7 | 24VDC | VF | - | - | 141-ES-205B | 141-PC-0105B | CHLR2_PMP_TRP | CHILLER-2 WATER PUMP TRIP STATUS | NORMAL | TRIP | I12.2 | XDI7-5 | XDI7-6
100 | IM2 | DI7 | 24VDC | VF | - | - | 141-ES-205B | 141-PC-0105B | CHLR2_PMP_RMT | CHILLER-2 WATER PUMP REMOTE MODE STATUS | LOCAL | REMOTE | I12.3 | XDI7-7 | XDI7-8
101 | IM2 | DI7 | 24VDC | VF | - | - | 141-ES-205B | 141-PC-0105B | CHLR2_PMP_ES | CHILLER-2 WATER PUMP EMERGENCY STOP | NORMAL | ACTIVE | I12.4 | XDI7-9 | XDI7-10
102 | IM2 | DI7 | 24VDC | VF | - | - | FIELD | - | AHU2-BFV-ZIO | MOTORIZED BUTTER FLY VALVE AHU-2 OPEN STATUS | NOT OPEN | OPEN | I12.5 | XDI7-11 | XDI7-12
103 | IM2 | DI7 | 24VDC | VF | - | - | FIELD | - | AHU2-BFV-ZIC | MOTORIZED BUTTER FLY VALVE AHU-2 CLOSE STATUS | NOT CLOSE | CLOSE | I12.6 | XDI7-13 | XDI7-14
104 | IM2 | DI7 | 24VDC | VF | - | - | FIELD | 141-GD-0222 | 141-GD-0222-ZIO | MOTORIZED SHUTOFF DAMPER 141-GD-0222 OPEN STATUS | NOT OPEN | OPEN | I12.7 | XDI7-15 | XDI7-16
105 | IM2 | DI7 | 24VDC | VF | - | - | FIELD | 141-GD-0222 | 141-GD-0222-ZIC | MOTORIZED SHUTOFF DAMPER 141-GD-0222 CLOSE STATUS | NOT CLOSE | CLOSE | I13.0 | XDI7-17 | XDI7-18
106 | IM2 | DI7 | 24VDC | VF | - | - | FIELD | 141-GD-0224 | 141-GD-0224-ZIO | MOTORIZED SHUTOFF DAMPER 141-GD-0224 OPEN STATUS | NOT OPEN | OPEN | I13.1 | XDI7-19 | XDI7-20
107 | IM2 | DI7 | 24VDC | VF | - | - | FIELD | 141-GD-0224 | 141-GD-0224-ZIC | MOTORIZED SHUTOFF DAMPER 141-GD-0224 CLOSE STATUS | NOT CLOSE | CLOSE | I13.2 | XDI7-21 | XDI7-22
108 | IM2 | DI7 | 24VDC | VF | - | - | FIELD | 141-GD-0227 | 141-GD-0227-ZIO | MOTORIZED SHUTOFF DAMPER 141-GD-0227 OPEN STATUS | NOT OPEN | OPEN | I13.3 | XDI7-23 | XDI7-24
109 | IM2 | DI7 | 24VDC | VF | - | - | FIELD | 141-GD-0227 | 141-GD-0227-ZIC | MOTORIZED SHUTOFF DAMPER 141-GD-0227 CLOSE STATUS | NOT CLOSE | CLOSE | I13.4 | XDI7-25 | XDI7-26
110 | IM2 | DI7 | 24VDC | VF | - | - | FIELD | 141-GD-0212 | 141-GD-0212-ZIO | MOTORIZED FIRE DAMPER 141-GD-0212 OPEN STATUS | NOT OPEN | OPEN | I13.5 | XDI7-27 | XDI7-28
111 | IM2 | DI7 | 24VDC | VF | - | - | FIELD | 141-GD-0212 | 141-GD-0212-ZIC | MOTORIZED FIRE DAMPER 141-GD-0212 CLOSE STATUS | NOT CLOSE | CLOSE | I13.6 | XDI7-29 | XDI7-30
112 | IM2 | DI7 | 24VDC | VF | - | - | FIELD | 141-GD-0213 | 141-GD-0213-ZIO | MOTORIZED FIRE DAMPER 141-GD-0213 OPEN STATUS | NOT OPEN | OPEN | I13.7 | XDI7-31 | XDI7-32
113 | IM2 | DI8 | 24VDC | VF | - | - | FIELD | 141-GD-0213 | 141-GD-0213-ZIC | MOTORIZED FIRE DAMPER 141-GD-0213 CLOSE STATUS | NOT CLOSE | CLOSE | I14.0 | XDI8-1 | XDI8-2
114 | IM2 | DI8 | 24VDC | VF | - | - | FIELD | 141-GD-0214 | 141-GD-0214-ZIO | MOTORIZED FIRE DAMPER 141-GD-0214 OPEN STATUS | NOT OPEN | OPEN | I14.1 | XDI8-3 | XDI8-4
115 | IM2 | DI8 | 24VDC | VF | - | - | FIELD | 141-GD-0214 | 141-GD-0214-ZIC | MOTORIZED FIRE DAMPER 141-GD-0214 CLOSE STATUS | NOT CLOSE | CLOSE | I14.2 | XDI8-5 | XDI8-6
116 | IM2 | DI8 | 24VDC | VF | - | - | FIELD | 141-GD-0215 | 141-GD-0215-ZIO | MOTORIZED FIRE DAMPER 141-GD-0215 OPEN STATUS | NOT OPEN | OPEN | I14.3 | XDI8-7 | XDI8-8
117 | IM2 | DI8 | 24VDC | VF | - | - | FIELD | 141-GD-0215 | 141-GD-0215-ZIC | MOTORIZED FIRE DAMPER 141-GD-0215 CLOSE STATUS | NOT CLOSE | CLOSE | I14.4 | XDI8-9 | XDI8-10
118 | IM2 | DI8 | 24VDC | VF | - | - | FIELD | 141-GB-0116 | UPS_HTR_TRP | UPS ROOM HEATER TRIP STATUS | NORMAL | TRIP | I14.5 | XDI8-11 | XDI8-12
119 | IM2 | DI8 | 24VDC | VF | - | - | FIELD | 141-GB-0116 | UPS_HTR_ON | UPS ROOM HEATER ON/OFF STATUS | OFF | ON | I14.6 | XDI8-13 | XDI8-14
120 | IM2 | DI8 | 24VDC | VF | - | - | FIELD | 141-GB-0117 | TLR_HTR_TRP | TELECOM ROOM HEATER TRIP STATUS | NORMAL | TRIP | I14.7 | XDI8-15 | XDI8-16
121 | IM2 | DI8 | 24VDC | VF | - | - | FIELD | 141-GB-0117 | TLR_HTR_ON | TELECOM HEATER ON/OFF STATUS | OFF | ON | I15.0 | XDI8-17 | XDI8-18
122 | IM2 | DI8 | 24VDC | VF | - | - | 141-ES-205B | - | INC1_ON | MAIN INCOMER-1 ON/OFF STATUS | OPEN | CLOSE | I15.1 | XDI8-19 | XDI8-20
123 | IM2 | DI8 | 24VDC | VF | - | - | 141-ES-205B | - | INC1_TRP | MAIN INCOMER-1 TRIP STATUS | NORMAL | TRIP | I15.2 | XDI8-21 | XDI8-22
124 | IM2 | DI8 | 24VDC | VF | - | - | 141-ES-205B | - | INC2_ON | MAIN INCOMER-2 ON/OFF STATUS | OPEN | CLOSE | I15.3 | XDI8-23 | XDI8-24
125 | IM2 | DI8 | 24VDC | VF | - | - | 141-ES-205B | - | INC2_TRP | MAIN INCOMER-2 TRIP STATUS | NORMAL | TRIP | I15.4 | XDI8-25 | XDI8-26
126 | IM2 | DI8 | 24VDC | VF | - | - | LFCP |  | HVAC_SHUT | HVAC SHUTDOWN COMMAND FROM F&G AND ALL DAMPERS CLOSE | NORMAL | SHUTDOWN | I15.5 | XDI8-27 | XDI8-28
127 | IM2 | DI8 | 24VDC | VF | - | - | LFCP |  | HVAC_RECR | HVAC RECIRCULATION MODE FROM F&G AND AIR INTAKE DAMPER CLOSE | NORMAL | RECIRCUL | I15.6 | XDI8-29 | XDI8-30
128 | IM2 | DI8 | 24VDC | VF | - | - | LFCP |  | HVAC_H2_HIGH | HVAC HYDROGEN HIGH IN BATTERY ROOM FROM F&G | NORMAL | H2 HIGH | I15.7 | XDI8-31 | XDI8-32
129 | IM2 | DI9 | 24VDC | VF | - | - | FIELD | 141-GB-0119 | HAVC_HTR_TRP | HVAC ROOM HEATER TRIP STATUS | NORMAL | TRIP | I16.0 | XDI9-1 | XDI9-2
130 | IM2 | DI9 | 24VDC | VF | - | - | FIELD | 141-GB-0119 | HVAC_HTR_ON | HVAC HEATER ON/OFF STATUS | OFF | ON | I16.1 | XDI9-3 | XDI9-4
131 | IM2 | DI9 | 24VDC | VF | - | - | 141-ES-205B | 141-GA-0105B | AHU2_FAN2_RUN | AHU-2 FAN-2 RUN STATUS | STOPPED | RUNNING | I16.2 | XDI9-5 | XDI9-6
132 | IM2 | DI9 | 24VDC | VF | - | - | 141-ES-205B | 141-GA-0105B | AHU2_FAN2_RMT | AHU-2 FAN-2 REMOTE MODE STATUS | LOCAL | REMOTE | I16.3 | XDI9-7 | XDI9-8
133 | IM2 | DI9 | 24VDC | VF | - | - | 141-ES-205B | 141-GA-0105B | AHU2_FAN2_BRK_TRP | AHU-2 FAN-2 BREAKER TRIP STATUS | NORMAL | TRIP | I16.4 | XDI9-9 | XDI9-10
134 | IM2 | DI9 | 24VDC | VF | - | - | - | - | CHLR2-BFV-ZIO | MOTORIZED BUTTER FLY VALVE CHILLER-2 OPEN STATUS | NOT OPEN | OPEN | I16.5 | XDI9-11 | XDI9-12
135 | IM2 | DI9 | 24VDC | VF | - | - | - | - | CHLR2-BFV-ZIC | MOTORIZED BUTTER FLY VALVE CHILLER-1 CLOSE STATUS | NOT CLOSE | CLOSE | I16.6 | XDI9-13 | XDI9-14
136 | IM2 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I16.7 | XDI9-15 | XDI9-16
137 | IM2 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.0 | XDI9-17 | XDI9-18
138 | IM2 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.1 | XDI9-19 | XDI9-20
139 | IM2 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.2 | XDI9-21 | XDI9-22
140 | IM2 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.3 | XDI9-23 | XDI9-24
141 | IM2 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.4 | XDI9-25 | XDI9-26
142 | IM2 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.5 | XDI9-27 | XDI9-28
143 | IM2 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.6 | XDI9-29 | XDI9-30
144 | IM2 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I17.7 | XDI9-31 | XDI9-32

## DO
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
SUBSTATION-02
RUWAIS - U.A.E.
[10 empty] | FACILITY NAME: BOROUGE 4 |  |  |  | COMPANY PROJ. NO. |  | 4700000897
[14 empty] | CONTRACTOR. PROJ. NO. |  | 083118C
|  | SS-02-HVAC-CP | [7 empty] | DOCUMENT TITLE: SS-02 HVAC PLC System - I/O List |  |  |  | SUBCONTR. ID |  | -
Sl. No. | IM Module | I/O Detail |  |  |  |  | TO | EQUIPMENT TAG | PLC TAG | Description | STATES |  | PLC Term. | TB GROUP |  | Verified & Signed
|  | Module | Supply | Type | Range | Unit |  |  |  |  | FALSE | TRUE
DIGITAL OUTPUT
1 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-205B | 141-GC-0105A | CHLR1_CMD | CHILLER-1 START/STOP COMMAND | STOP | START | Q0.0 | XDO1-1 | XDO1-2
2 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-205B | 141-GC-0105A | CHLR1_INTL_CMD | CHILLER-1 PUMP INTERLOCK COMMAND | OFF | ON | Q0.1 | XDO1-3 | XDO1-4
3 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-205B | 141-GC-0105A | CHLR1_DL_CMD | CHILLER-1 DEMAND LIMIT COMMAND | OFF | ON | Q0.2 | XDO1-5 | XDO1-6
4 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-205B | 141-GA-0105A | AHU1_FAN1_CMD | AHU-1 FAN-1 START/STOP COMMAND | STOP | START | Q0.3 | XDO1-7 | XDO1-8
5 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-205B | 141-GK-0103A | BAT_FAN1_CMD | BATTERY ROOM EXHAUST FAN-1 START/STOP COMMAND | STOP | START | Q0.4 | XDO1-9 | XDO1-10
6 | IM1 | DO1 | 24VDC | 240V | - | - | 141-ES-205B | - | AHU1_MBFV_OPN | AHU-1 MOTORIZED BUTTER FLY VALVE OPEN COMMAND | NOT OPEN | OPEN | Q0.5 | XDO1-11 | XDO1-12
7 | IM1 | DO1 | 24VDC | 240V | - | - | 141-ES-205B | - | AHU1_MBFV_CLS | AHU-1 MOTORIZED BUTTER FLY VALVE CLOSE COMMAND | NOT CLOSE | CLOSE | Q0.6 | XDO1-13 | XDO1-14
8 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-205B | 141-PC-0105A | CHLR1_PMP_CMD | CHILLER-1 WATER PUMP START/STOP COMMAND | STOP | START | Q0.7 | XDO1-15 | XDO1-16
9 | IM1 | DO1 | 24VDC | 24VAC | - | - | FIELD | 141-GD-0221 | 141-GD-0221-CMD | MOTORIZED SHUTOFF DAMPER 141-GD-0221 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q1.0 | XDO1-17 | XDO1-18
10 | IM1 | DO1 | 24VDC | 24VAC | - | - | FIELD | 141-GD-0223 | 141-GD-0223-CMD | MOTORIZED SHUTOFF DAMPER 141-GD-0223 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q1.1 | XDO1-19 | XDO1-20
11 | IM1 | DO1 | 24VDC | 24VAC | - | - | FIELD | 141-GD-0226 | 141-GD-0226-CMD | MOTORIZED SHUTOFF DAMPER 141-GD-0226 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q1.2 | XDO1-21 | XDO1-22
12 | IM1 | DO1 | 24VDC | 24VAC | - | - | FIELD | 141-GD-0201 | 141-GD-0201-CMD | MOTORIZED GAS DAMPER 141-GD-0201 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q1.3 | XDO1-23 | XDO1-24
13 | IM1 | DO1 | 24VDC | 24VAC | - | - | FIELD | 141-GD-0202 | 141-GD-0202-CMD | MOTORIZED FIRE DAMPER 141-GD-0202 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q1.4 | XDO1-25 | XDO1-26
14 | IM1 | DO1 | 24VDC | 24VAC | - | - | FIELD | 141-GD-0203 | 141-GD-0203-CMD | MOTORIZED FIRE DAMPER 141-GD-0203 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q1.5 | XDO1-27 | XDO1-28
15 | IM1 | DO1 | 24VDC | 24VAC | - | - | FIELD | 141-GD-0204 | 141-GD-0204-CMD | MOTORIZED FIRE DAMPER 141-GD-0204 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q1.6 | XDO1-29 | XDO1-30
16 | IM1 | DO1 | 24VDC | 24VAC | - | - | FIELD | 141-GD-0205 | 141-GD-0205-CMD | MOTORIZED FIRE DAMPER 141-GD-0205 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q1.7 | XDO1-31 | XDO1-32
17 | IM1 | DO2 | 24VDC | 24VAC | - | - | FIELD | 141-GD-0206 | 141-GD-0206-CMD | MOTORIZED FIRE DAMPER 141-GD-0206 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q2.0 | XDO2-1 | XDO2-2
18 | IM1 | DO2 | 24VDC | 24VAC | - | - | FIELD | 141-GD-0207 | 141-GD-0207-CMD | MOTORIZED FIRE DAMPER 141-GD-0207 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q2.1 | XDO2-3 | XDO2-4
19 | IM1 | DO2 | 24VDC | 24VAC | - | - | FIELD | 141-GD-0208 | 141-GD-0208-CMD | MOTORIZED FIRE DAMPER 141-GD-0208 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q2.2 | XDO2-5 | XDO2-6
20 | IM1 | DO2 | 24VDC | 24VAC | - | - | FIELD | 141-GD-0209 | 141-GD-0209-CMD | MOTORIZED FIRE DAMPER 141-GD-0209 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q2.3 | XDO2-7 | XDO2-8
21 | IM1 | DO2 | 24VDC | 24VAC | - | - | FIELD | 141-GD-0210 | 141-GD-0210-CMD | MOTORIZED FIRE DAMPER 141-GD-0210 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q2.4 | XDO2-9 | XDO2-10
22 | IM1 | DO2 | 24VDC | 24VAC | - | - | FIELD | 141-GD-0211 | 141-GD-0211-CMD | MOTORIZED FIRE DAMPER 141-GD-0211 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q2.5 | XDO2-11 | XDO2-12
23 | IM1 | DO2 | 24VDC | 24VAC | - | - | FIELD | 141-GD-0212 | 141-GD-0212-CMD | MOTORIZED FIRE DAMPER 141-GD-0212 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q2.6 | XDO2-13 | XDO2-14
24 | IM1 | DO2 | 24VDC | 24VAC | - | - | FIELD | 141-GD-0213 | 141-GD-0213-CMD | MOTORIZED FIRE DAMPER 141-GD-0213 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q2.7 | XDO2-15 | XDO2-16
25 | IM1 | DO2 | 24VDC | 24VDC | - | - | 141-ES-205A | - | BUZZ_ON | BUZZER ON COMMAND | OFF | ON | Q3.0 | XDO2-17 | XDO2-18
26 | IM1 | DO2 | 24VDC | VF | - | - | LFCP | - | HVAC_SHUT_FG | HVAC SHUTDOWN FEEDBACK TO LFCP | OFF | ON | Q3.1 | XDO2-19 | XDO2-20
27 | IM1 | DO2 | 24VDC | VF | - | - | LFCP | - | HVAC_SHUT_FG | RECIRCULATION FEEDBACK TO LFCP | OFF | ON | Q3.2 | XDO2-21 | XDO2-22
28 | IM1 | DO2 | 24VDC | VF | - | - | 141-ES-205B | 141-GF-0110 | BLEED_CMD | BLEED FAN START/STOP COMMAND | STOP | START | Q3.3 | XDO2-23 | XDO2-24
29 | IM1 | DO2 | 24VDC | VF | - | - | 141-ES-001B | 141-GA-0105A | AHU1_FAN2_CMD | AHU-1 FAN-2 START/STOP COMMAND | STOP | START | Q3.4 | XDO2-25 | XDO2-26
30 | IM1 | DO2 | 24VDC | VF | - | - | - | - | CHLR1_MBFV_OPN | CHILLER-1 MOTORIZED BUTTER FLY VALVE OPEN COMMAND | NOT OPEN | OPEN | Q3.5 | XDO2-27 | XDO2-28
31 | IM1 | DO2 | 24VDC | VF | - | - | - | - | CHLR1_MBFV_CLS | CHILLER-1 MOTORIZED BUTTER FLY VALVE CLOSE COMMAND | NOT CLOSE | CLOSE | Q3.6 | XDO2-29 | XDO2-30
32 | IM1 | DO2 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | Q3.7 | XDO2-31 | XDO2-32
33 | IM2 | DO3 | 24VDC | VF | - | - | 141-ES-205B | 141-GC-0105B | CHLR2_CMD | CHILLER-2 START/STOP COMMAND | STOP | START | Q4.0 | XDO3-1 | XDO3-2
34 | IM2 | DO3 | 24VDC | VF | - | - | 141-ES-205B | 141-GC-0105B | CHLR2_INTL_CMD | CHILLER-2 PUMP INTERLOCK COMMAND | OFF | ON | Q4.1 | XDO3-3 | XDO3-4
35 | IM2 | DO3 | 24VDC | VF | - | - | 141-ES-205B | 141-GC-0105B | CHLR2_DL_CMD | CHILLER-2 DEMAND LIMIT COMMAND | OFF | ON | Q4.2 | XDO3-5 | XDO3-6
36 | IM2 | DO3 | 24VDC | VF | - | - | 141-ES-205B | 141-GA-0105B | AHU2_FAN1_CMD | AHU-2 FAN-1 START/STOP COMMAND | STOP | START | Q4.3 | XDO3-7 | XDO3-8
37 | IM2 | DO3 | 24VDC | VF | - | - | 141-ES-205B | 141-GA-0105B | BAT_FAN2_CMD | BATTERY ROOM EXHAUST FAN-2 START/STOP COMMAND | STOP | START | Q4.4 | XDO3-9 | XDO3-10
38 | IM2 | DO3 | 24VDC | 240V | - | - | 141-ES-205B | - | AHU2_MBFV_OPN | AHU-2 MOTORIZED BUTTER FLY VALVE OPEN COMMAND | NOT OPEN | OPEN | Q4.5 | XDO3-11 | XDO3-12
39 | IM2 | DO3 | 24VDC | 240V | - | - | 141-ES-205B | - | AHU2_MBFV_CLS | AHU-2 MOTORIZED BUTTER FLY VALVE CLOSE COMMAND | NOT CLOSE | CLOSE | Q4.6 | XDO3-13 | XDO3-14
40 | IM2 | DO3 | 24VDC | VF | - | - | 141-ES-205B | 141-PC-0105B | CHLR2_PMP_CMD | CHILLER-2 WATER PUMP START/STOP COMMAND | STOP | START | Q4.7 | XDO3-15 | XDO3-16
41 | IM2 | DO3 | 24VDC | 24VAC | - | - | FIELD | 141-GD-0222 | 141-GD-0222-CMD | MOTORIZED SHUTOFF DAMPER 141-GD-0222 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q5.0 | XDO3-17 | XDO3-18
42 | IM2 | DO3 | 24VDC | 24VAC | - | - | FIELD | 141-GD-0224 | 141-GD-0224-CMD | MOTORIZED SHUTOFF DAMPER 141-GD-0224 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q5.1 | XDO3-19 | XDO3-20
43 | IM2 | DO3 | 24VDC | 24VAC | - | - | FIELD | 141-GD-0227 | 141-GD-0227-CMD | MOTORIZED SHUTOFF DAMPER 141-GD-0227 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q5.2 | XDO3-21 | XDO3-22
44 | IM2 | DO3 | 24VDC | 24VAC | - | - | FIELD | 141-GD-0214 | 141-GD-0214-CMD | MOTORIZED FIRE DAMPER 141-GD-0214 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q5.3 | XDO3-23 | XDO3-24
45 | IM2 | DO3 | 24VDC | 24VAC | - | - | FIELD | 141-GD-0215 | 141-GD-0215-CMD | MOTORIZED FIRE DAMPER 141-GD-0215 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q5.4 | XDO3-25 | XDO3-26
46 | IM2 | DO3 | 24VDC | VF | - | - | 141-ES-205B | 141-GA-0105B | AHU2_FAN2_CMD | AHU-2 FAN-2 START/STOP COMMAND | STOP | START | Q5.5 | XDO3-27 | XDO3-28
47 | IM2 | DO3 | 24VDC | VF | - | - | - | - | CHLR2_MBFV_OPN | CHILLER-2 MOTORIZED BUTTER FLY VALVE OPEN COMMAND | NOT OPEN | OPEN | Q5.6 | XDO3-29 | XDO3-30
48 | IM2 | DO3 | 24VDC | VF | - | - | - | - | CHLR2_MBFV_CLS | CHILLER-2 MOTORIZED BUTTER FLY VALVE CLOSE COMMAND | NOT CLOSE | CLOSE | Q5.7 | XDO3-31 | XDO3-32

## AI
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
SUBSTATION-02
RUWAIS - U.A.E.
[10 empty] | FACILITY NAME: BOROUGE 4 | [5 empty] | COMPANY PROJ. NO. |  | 4700000897
[16 empty] | CONTRACTOR. PROJ. NO. |  | 083118C
| SS-02-HVAC-CP | [8 empty] | DOCUMENT TITLE: SS-02 HVAC PLC System - I/O List | [5 empty] | SUBCONTR. ID |  | -
Sl. No. | IM Module | I/O Detail |  |  |  |  | FROM | EQUIPMENT TAG | PLC TAG | Description | Alarm Setpoints |  |  |  | PLC Term. | TB GROUP |  | Verified & Signed
|  | Module | Supply | Type | Range | Unit |  |  |  |  | LL | L | H | HH
ANALOGUE INPUT
1 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | 141-DPIT-0201 | DPIT-1 | DIFFERENTIAL PRESSURE FRESH AIR DUCT | - | 1 | 5 | - | I0+/I0- | XAI1-1 | XAI1-2
2 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | 141-DPIT-0202 | DPIT-2 | DIFFERENTIAL PRESSURE HVAC ROOM | - | 1 | 5 | - | I1+/I1- | XAI1-3 | XAI1-4
3 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | 141-DPIT-0203 | DPIT-3 | DIFFERENTIAL PRESSURE LV SWT. GR. ROOM | - | 1 | 5 | - | I2+/I2- | XAI1-5 | XAI1-6
4 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | 141-DPIT-0204 | DPIT-4 | DIFFERENTIAL PRESSURE LV SWT. GR. AIRLOCK ROOM | - | 1 | 5 | - | I3+/I3- | XAI1-7 | XAI1-8
5 | IM1 | AI1 | 24VDC | Sink | 0-55 | °C | FIELD | 141-TT-0201 | TT-001 | FRESH AIR DUCT TEMPERATURE | - | 20 | 30 | - | I4+/I4- | XAI1-9 | XAI1-10
6 | IM1 | AI1 | 24VDC | Sink | 0-55 | °C | FIELD | 141-TT-0202 | TT-002 | COMMON SUPPLY AIR DUCT TEMPERATURE | - | 20 | 30 | - | I5+/I5- | XAI1-11 | XAI1-12
7 | IM1 | AI1 | 24VDC | Sink | 0-55 | °C | FIELD | 141-TT-0203 | TT-003 | COMMON RETURN AIR DUCT TEMPERATURE | - | 20 | 30 | - | I6+/I6- | XAI1-13 | XAI1-14
8 | IM1 | AI1 | 24VDC | Sink | 0-55 | °C | FIELD | 141-TT-0204 | TT-004 | HVAC ROOM TEMPERATURE | - | 20 | 30 | - | I7+/I7- | XAI1-15 | XAI1-16
9 | IM1 | AI2 | 24VDC | Sink | 0-55 | °C | FIELD | 141-TT-0205 | TT-005 | LV SWT. GR. ROOM TEMPERATURE | - | 20 | 30 | - | I0+/I0- | XAI2-1 | XAI2-2
10 | IM1 | AI2 | 24VDC | Sink | 0-100 | RH | FIELD | 141-HT-0201 | HT-001 | COMMON RETURN AIR DUCT HUMIDITY | - | 30 | 60 | - | I1+/I1- | XAI2-3 | XAI2-4
11 | IM1 | AI2 | 24VDC | Sink | 0-100 | RH | FIELD | 141-HT-0202 | HT-002 | HVAC ROOM HUMIDITY | - | 30 | 60 | - | I2+/I2- | XAI2-5 | XAI2-6
12 | IM1 | AI2 | 24VDC | Sink | 0-100 | RH | FIELD | 141-HT-0203 | HT-003 | LV SWT. GR. ROOM HUMIDITY | - | 30 | 60 | - | I3+/I3- | XAI2-7 | XAI2-8
13 | IM1 | AI2 | 24VDC | Sink | 0-100 | RH | FIELD | 141-HT-0204 | HT-004 | RACK ROOM HUMIDITY | - | 30 | 60 | - | I4+/I4- | XAI2-9 | XAI2-10
14 | IM1 | AI2 | 24VDC | Sink | 0-100 | RH | FIELD | 141-HT-0205 | HT-005 | TELECOM ROOM HUMIDITY | - | 30 | 60 | - | I5+/I5- | XAI2-11 | XAI2-12
15 | IM1 | AI2 | 24VDC | Sink | 0-50 | HZ | FIELD | 141-PC-0105A | CHLR1-PMP-SPD-FB | CHILLER-1 WATER PUMP SPEED FEEDBACK | - | - | - | - | I6+/I6- | XAI2-13 | XAI2-14
16 | IM1 | AI2 | 24VDC | Sink | 0-100 | % | FIELD | 141-GD-0225 | 141-GD-0225-FB | MODULATING FRESH AIR DAMPER GD-0225 POSITION FEEDBACK | - | - | - | - | I7+/I7- | XAI2-15 | XAI2-16
17 | IM1 | AI3 | 24VDC | Sink | 0-50 | HZ | 141-ES-205B | 141-GA-0105A | AHU1-FAN1-SPD-FB | AHU-1 FAN-1 SPEED FEEDBACK | - | - | - | - | I0+/I0- | XAI3-1 | XAI3-2
18 | IM1 | AI3 | 24VDC | Sink | 0-50 | HZ | 141-ES-205B | 141-GA-0105A | AHU1-FAN2-SPD-FB | AHU-1 FAN-2 SPEED FEEDBACK | - | - | - | - | I1+/I1- | XAI3-3 | XAI3-4
19 | IM1 | AI3 | 24VDC | Sink | 0-100 | % | TCV | AHU-A-TCV | AHU-A-TCV-FB | AHU A 3 WAY TCV POSITION FEEDBACK | - | - | - | - | I2+/I2- | XAI3-5 | XAI3-6
20 | IM1 | AI3 | 24VDC | Sink | - | - | FIELD | - |  | SPARE | - | - | - | - | I3+/I3- | XAI3-7 | XAI3-8
21 | IM1 | AI3 | 24VDC | Sink | - | - | FIELD | - |  | SPARE | - | - | - | - | I4+/I4- | XAI3-9 | XAI3-10
22 | IM1 | AI3 | 24VDC | Sink | - | - | FIELD | - |  | SPARE | - | - | - | - | I5+/I5- | XAI3-11 | XAI3-12
23 | IM1 | AI3 | 24VDC | Sink | - | - | FIELD | - |  | SPARE | - | - | - | - | I6+/I6- | XAI3-13 | XAI3-14
24 | IM1 | AI3 | 24VDC | Sink | - | - | FIELD | - |  | SPARE | - | - | - | - | I7+/I7- | XAI3-15 | XAI3-16
25 | IM2 | AI4 | 24VDC | Sink | 0-6 | pa | FIELD | 141-DPIT-0205 | DPIT-5 | DIFFERENTIAL PRESSURE RACK ROOM | - | 1 | 5 | - | I0+/I0- | XAI4-1 | XAI4-2
26 | IM2 | AI4 | 24VDC | Sink | 0-6 | pa | FIELD | 141-DPIT-0206 | DPIT-6 | DIFFERENTIAL PRESSURE RACK AIRLOCK ROOM | - | 1 | 5 | - | I1+/I1- | XAI4-3 | XAI4-4
27 | IM2 | AI4 | 24VDC | Sink | 0-6 | pa | FIELD | 141-DPIT-0207 | DPIT-7 | DIFFERENTIAL PRESSURE TELECOM ROOM | - | 1 | 5 | - | I2+/I2- | XAI4-5 | XAI4-6
28 | IM2 | AI4 | 24VDC | Sink | 0-6 | pa | FIELD | 141-DPIT-0208 | DPIT-8 | DIFFERENTIAL PRESSURE BATTERY ROOM | - | 1 | 5 | - | I3+/I3- | XAI4-7 | XAI4-8
29 | IM2 | AI4 | 24VDC | Sink | 0-55 | °C | FIELD | 141-TT-0206 | TT-006 | RACK ROOM TEMPERATURE | - | 20 | 30 | - | I4+/I4- | XAI4-9 | XAI4-10
30 | IM2 | AI4 | 24VDC | Sink | 0-55 | °C | FIELD | 141-TT-0207 | TT-007 | TELECOM ROOM TEMPERATURE | - | 20 | 30 | - | I5+/I5- | XAI4-11 | XAI4-12
31 | IM2 | AI4 | 24VDC | Sink | 0-55 | °C | FIELD | 141-TT-0208 | TT-008 | UPS ROOM TEMPERATURE | - | 20 | 30 | - | I6+/I6- | XAI4-13 | XAI4-14
32 | IM2 | AI4 | 24VDC | Sink | 0-55 | °C | FIELD | 141-TT-0209 | TT-009 | BATTERY ROOM TEMPERATURE | - | 20 | 30 | - | I7+/I7- | XAI4-15 | XAI4-16
33 | IM2 | AI5 | 24VDC | Sink | 0-100 | RH | FIELD | 141-HT-0206 | HT-006 | UPS ROOM HUMIDITY | - | 30 | 60 | - | I0+/I0- | XAI5-1 | XAI5-2
34 | IM2 | AI5 | 24VDC | Sink | 0-100 | RH | FIELD | 141-HT-0207 | HT-007 | BATTERY ROOM HUMIDITY | - | 30 | 60 | - | I1+/I1- | XAI5-3 | XAI5-4
35 | IM2 | AI5 | 24VDC | Sink | 0-50 | HZ | FIELD | 141-PC-0105B | CHLR2-PMP-SPD-FB | CHILLER-2 WATER PUMP SPEED FEEDBACK | - | - | - | - | I2+/I2- | XAI5-5 | XAI5-6
36 | IM2 | AI5 | 24VDC | Sink | 0-50 | HZ | 141-ES-205B | 141-GA-0105B | AHU2-FAN1-SPD-FB | AHU-2 FAN-1 SPEED FEEDBACK | - | - | - | - | I3+/I3- | XAI5-7 | XAI5-8
37 | IM2 | AI5 | 24VDC | Sink | 0-50 | HZ | 141-ES-205B | 141-GA-0105B | AHU2-FAN2-SPD-FB | AHU-2 FAN-2 SPEED FEEDBACK | - | - | - | - | I4+/I4- | XAI5-9 | XAI5-10
38 | IM2 | AI5 | 24VDC | Sink | 0-100 | % | TCV | AHU-A-TCV | AHU-A-TCV-FB | AHU A 3 WAY TCV POSITION FEEDBACK | - | - | - | - | I5+/I5- | XAI5-11 | XAI5-12
39 | IM2 | AI5 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I6+/I6- | XAI5-13 | XAI5-14
40 | IM2 | AI5 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I7+/I7- | XAI5-15 | XAI5-16

## AO
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
SUBSTATION-02
RUWAIS - U.A.E.
[10 empty] | FACILITY NAME: BOROUGE 4 | [5 empty] | COMPANY PROJ. NO. |  | 4700000897
[16 empty] | CONTRACTOR. PROJ. NO. |  | 083118C
| SS-02-HVAC-CP | [8 empty] | DOCUMENT TITLE: SS-02 HVAC PLC System - I/O List | [5 empty] | SUBCONTR. ID |  | -
Sl. No. | IM Module | I/O Detail |  |  |  |  | TO | EQUIPMENT TAG | PLC TAG | Description | Alarm Setpoints |  |  |  | PLC Term. | TB GROUP |  | Verified & Signed
|  | Module | Supply | Type | Range | Unit |  |  |  |  | LL | L | H | HH
ANALOGUE OUTPUT
1 | IM1 | AO1 | 24VDC | 4-20mA | - | - | AHU-1 | 141-GA-0105A | AHU1-FAN1-SPD-REF | AHU-1 FAN-1 SPEED SETPOINT | - | - | - | - | Q0+/Q0- | XAO1-1 | XAO1-2
2 | IM1 | AO1 | 24VDC | 4-20mA | - | - | AHU-1 | 141-GA-0105A | AHU1-FAN2-SPD-REF | AHU-1 FAN-2 SPEED SETPOINT | - | - | - | - | Q1+/Q1- | XAO1-3 | XAO1-4
3 | IM1 | AO1 | 24VDC | 4-20mA | - | - | CWP | 141-PC-0105A | CHLR1-PMP-SPD-REF | CHILLER-1 WATER PUMP SPEED SETPOINT | - | - | - | - | Q2+/Q2- | XAO1-5 | XAO1-6
4 | IM1 | AO1 | 24VDC | 4-20mA | - | - | - | 141-GD-0225 | 141-GD-0335-SP | MODULATING FRESH AIR DAMPER MD-0335 SETPOINT | - | - | - | - | Q3+/Q3- | XAO1-7 | XAO1-8
5 | IM1 | AO2 | 24VDC | 4-20mA | - | - | TCV | AHU-A-TCV | AHU-A-TCV-SP | AHU A 3 WAY TCV SETPOINT | - | - | - | - | Q2+/Q2- | XAO2-5 | XAO2-6
6 | IM1 | AO2 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q3+/Q3- | XAO2-7 | XAO2-8
7 | IM1 | AO2 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q3+/Q3- | XAO2-7 | XAO2-8
8 | IM1 | AO2 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q3+/Q3- | XAO2-7 | XAO2-8
9 | IM2 | AO3 | 24VDC | 4-20mA | - | - | AHU-2 | 141-GA-0105B | AHU2-FAN1-SPD-REF | AHU-2 FAN-1 SPEED SETPOINT | - | - | - | - | Q2+/Q2- | XAO2-5 | XAO2-6
10 | IM2 | AO3 | 24VDC | 4-20mA | - | - | AHU-2 | 141-GA-0105B | AHU2-FAN2-SPD-REF | AHU-2 FAN-2 SPEED SETPOINT | - | - | - | - | Q3+/Q3- | XAO2-7 | XAO2-8
11 | IM2 | AO3 | 24VDC | 4-20mA | - | - | CWP | 141-PC-0105B | CHLR2-PMP-SPD-REF | CHILLER-2 WATER PUMP SPEED SETPOINT | - | - | - | - | Q3+/Q3- | XAO2-7 | XAO2-8
12 | IM2 | AO3 | 24VDC | 4-20mA | - | - | TCV | AHU-B-TCV | AHU-B-TCV-SP | AHU B 3 WAY TCV SETPOINT | - | - | - | - | Q3+/Q3- | XAO2-7 | XAO2-8
13 | IM2 | AO4 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q2+/Q2- | XAO2-5 | XAO2-6
14 | IM2 | AO4 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q3+/Q3- | XAO2-7 | XAO2-8
15 | IM2 | AO4 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q3+/Q3- | XAO2-7 | XAO2-8
16 | IM2 | AO4 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q3+/Q3- | XAO2-7 | XAO2-8

## IO Summary
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
SUBSTATION-02
RUWAIS - U.A.E.
[8 empty] | FACILITY NAME: BOROUGE 4 | COMPANY PROJ. NO. | 4700000897
[9 empty] | CONTRACTOR. PROJ. NO. | 083118C
SS-02-HVAC-CP | [7 empty] | DOCUMENT TITLE: SS-01 HVAC PLC System - I/O List | SUBCONTR. ID | -
IO SUMMARY
Sl.No | Type | No. Of Channels | No. Of Modules | Count | Used | Spare | Spare %
1 | DI | 16 | 9 | 144 | 125 | 19 | 25.8427
3 | DO | 16 | 3 | 48 | 47 | 1 | 71.4286
4 | AI | 8 | 5 | 40 | 33 | 7 | 14.2857
5 | AO | 4 | 4 | 16 | 9 | 7 | 33.3333

## MODBUS_LIST
SUBSTATION-02 HVAC DCS INTERFACE SIGNALS
S.NO | EQUIPMENT TAG | TAG NAME | DESSCRIPTION | MULTIPLICATION FACTOR | DATA TYPE | SIGNAL FROM | SIGNAL TO | STATE 0 | STATE 1 | MODBUS ADDRESS | BIT | REMARKS
1 | 141-GC-0105A | CHLR1_RUN | CHILLER-1 UNIT RUN STATUS |  | BOOL | PLC | DCS | STOPPED | RUNNING | 40001 | 0
2 | 141-GC-0105A | CHLR1_TRP | CHILLER-1 UNIT TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40001 | 1
3 | 141-GC-0105A | CHLR1_RMT | CHILLER-1 REMOTE MODE STATUS |  | BOOL | PLC | DCS | LOCAL | REMOTE | 40001 | 2
4 | 141-GC-0105A | CHLR1_BRK_TRP | CHILLER-1 UNIT BREAKER TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40001 | 3
5 | 141-GC-0105A | CHLR1_FS | CHILLER-1 FLOW SWITCH STATUS |  | BOOL | PLC | DCS | NO FLOW | FLOW ON | 40001 | 4
6 | 141-GA-0105A | AHU1_FAN1_RUN | AHU-1 FAN-1 RUN STATUS |  | BOOL | PLC | DCS | STOPPED | RUNNING | 40001 | 5
7 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40001 | 6
8 | 141-GA-0105A | AHU1_FAN1_RMT | AHU-1 FAN-1 REMOTE MODE STATUS |  | BOOL | PLC | DCS | LOCAL | REMOTE | 40001 | 7
9 | 141-GA-0105A | AHU1_FAN1_BRK_TRP | AHU-1 FAN-1 UNIT BREAKER TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40001 | 8
10 | 141-GA-0105A | AHU1_PF_DPS | AHU-1 PRE-FILTER DIFFERENTIAL PRESSURE HIGH |  | BOOL | PLC | DCS | NORMAL | ALARM | 40001 | 9
11 | 141-GA-0105A | AHU1_FF_DPS | AHU-1 FINE-FILTER DIFFERENTIAL PRESSURE HIGH |  | BOOL | PLC | DCS | NORMAL | ALARM | 40001 | 10
12 | 141-GA-0105A | AHU1_AF_DPS | AHU-1 FAN AIR FLOW DIFFERENTIAL PRESSURE |  | BOOL | PLC | DCS | NO FLOW | FLOW ON | 40001 | 11
13 | 141-GK-0103A | BAT_FAN1_RUN | BATTERY ROOM FAN-1 RUN STATUS |  | BOOL | PLC | DCS | STOPPED | RUNNING | 40001 | 12
14 | 141-GK-0103A | BAT_FAN1_TRP | BATTERY ROOM FAN-1 TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40001 | 13
15 | 141-GK-0103A | BAT_FAN1_RMT | BATTERY ROOM FAN-1 REMOTE MODE STATUS |  | BOOL | PLC | DCS | LOCAL | REMOTE | 40001 | 14
16 | 141-GK-0103A | BAT_FAN1_ES | BATTERY ROOM FAN-1 EMERGENCY STOP |  | BOOL | PLC | DCS | NORMAL | ACTIVE | 40001 | 15
17 | 141-GK-0103A | BAT_FAN1_DPS | DIFFERENTIAL PRESSURE ACROSS BATTERY ROOM FAN-1 |  | BOOL | PLC | DCS | NO FLOW | FLOW ON | 40002 | 0
18 | 141-PC-0105A | CHLR1_PMP_RUN | CHILLER-1 WATER PUMP RUN STATUS |  | BOOL | PLC | DCS | STOPPED | RUNNING | 40002 | 1
19 | 141-PC-0105A | CHLR1_PMP_TRP | CHILLER-1 WATER PUMP TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40002 | 2
20 | 141-PC-0105A | CHLR1_PMP_RMT | CHILLER-1 WATER PUMP REMOTE MODE STATUS |  | BOOL | PLC | DCS | LOCAL | REMOTE | 40002 | 3
21 | 141-PC-0105A | CHLR1_PMP_ES | CHILLER-1 WATER PUMP EMERGENCY STOP |  | BOOL | PLC | DCS | NORMAL | ACTIVE | 40002 | 4
22 | - | BLD_FAN_RUN | BLEED FAN RUN STATUS |  | BOOL | PLC | DCS | STOPPED | RUNNING | 40002 | 5
23 | - | BLD_FAN_TRP | BLEED FAN TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40002 | 6
24 | - | BLD_FAN_RMT | BLEED FAN REMOTE MODE STATUS |  | BOOL | PLC | DCS | LOCAL | REMOTE | 40002 | 7
25 | - | BLD_FAN_ES | BLEED FAN EMERGENCY STOP |  | BOOL | PLC | DCS | NORMAL | ACTIVE | 40002 | 8
26 | - | AHU1-BFV-ZIO | MOTORIZED BUTTER FLY VALVE AHU-1 OPEN STATUS |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40002 | 9
27 | - | AHU1-BFV-ZIC | MOTORIZED BUTTER FLY VALVE AHU-1 CLOSE STATUS |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40002 | 10
28 | 141-GD-0221 | 141-GD-0221-ZIO | MOTORIZED SHUTOFF DAMPER 141-GD-0221 OPEN STATUS |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40002 | 11
29 | 141-GD-0221 | 141-GD-0221-ZIC | MOTORIZED SHUTOFF DAMPER 141-GD-0221 CLOSE STATUS |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40002 | 12
30 | 141-GD-0223 | 141-GD-0223-ZIO | MOTORIZED SHUTOFF DAMPER 141-GD-0223 OPEN STATUS |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40002 | 13
31 | 141-GD-0223 | 141-GD-0223-ZIC | MOTORIZED SHUTOFF DAMPER 141-GD-0223 CLOSE STATUS |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40002 | 14
32 | 141-GD-0226 | 141-GD-0226-ZIO | MOTORIZED SHUTOFF DAMPER 141-GD-0226 OPEN STATUS |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40002 | 15
33 | 141-GD-0226 | 141-GD-0226-ZIC | MOTORIZED SHUTOFF DAMPER 141-GD-0226 CLOSE STATUS |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40003 | 0
34 | 141-GD-0201 | 141-GD-0201-ZIO | MOTORIZED GAS DAMPER 141-GD-0201 OPEN STATUS |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40003 | 1
35 | 141-GD-0201 | 141-GD-0201-ZIC | MOTORIZED GAS DAMPER 141-GD-0201 CLOSE STATUS |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40003 | 2
36 | 141-GD-0202 | 141-GD-0202-ZIO | MOTORIZED FIRE DAMPER 141-GD-0202 OPEN STATUS |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40003 | 3
37 | 141-GD-0202 | 141-GD-0202-ZIC | MOTORIZED FIRE DAMPER 141-GD-0202 CLOSE STATUS |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40003 | 4
38 | 141-GD-0203 | 141-GD-0203-ZIO | MOTORIZED FIRE DAMPER 141-GD-0203 OPEN STATUS |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40003 | 5
39 | 141-GD-0203 | 141-GD-0203-ZIC | MOTORIZED FIRE DAMPER 141-GD-0203 CLOSE STATUS |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40003 | 6
40 | 141-GD-0204 | 141-GD-0204-ZIO | MOTORIZED FIRE DAMPER 141-GD-0204 OPEN STATUS |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40003 | 7
41 | 141-GD-0204 | 141-GD-0204-ZIC | MOTORIZED FIRE DAMPER 141-GD-0204 CLOSE STATUS |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40003 | 8
42 | 141-GD-0205 | 141-GD-0205-ZIO | MOTORIZED FIRE DAMPER 141-GD-0205 OPEN STATUS |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40003 | 9
43 | 141-GD-0205 | 141-GD-0205-ZIC | MOTORIZED FIRE DAMPER 141-GD-0205 CLOSE STATUS |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40003 | 10
44 | 141-GD-0206 | 141-GD-0206-ZIO | MOTORIZED FIRE DAMPER 141-GD-0206 OPEN STATUS |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40003 | 11
45 | 141-GD-0206 | 141-GD-0206-ZIC | MOTORIZED FIRE DAMPER 141-GD-0206 CLOSE STATUS |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40003 | 12
46 | 141-GD-0207 | 141-GD-0207-ZIO | MOTORIZED FIRE DAMPER 141-GD-0207 OPEN STATUS |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40003 | 13
47 | 141-GD-0207 | 141-GD-0207-ZIC | MOTORIZED FIRE DAMPER 141-GD-0207 CLOSE STATUS |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40003 | 14
48 | 141-GD-0208 | 141-GD-0208-ZIO | MOTORIZED FIRE DAMPER 141-GD-0208 OPEN STATUS |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40003 | 15
49 | 141-GD-0208 | 141-GD-0208-ZIC | MOTORIZED FIRE DAMPER 141-GD-0208 CLOSE STATUS |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40004 | 0
50 | 141-GD-0209 | 141-GD-0209-ZIO | MOTORIZED FIRE DAMPER 141-GD-0209 OPEN STATUS |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40004 | 1
51 | 141-GD-0209 | 141-GD-0209-ZIC | MOTORIZED FIRE DAMPER 141-GD-0209 CLOSE STATUS |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40004 | 2
52 | 141-GD-0210 | 141-GD-0210-ZIO | MOTORIZED FIRE DAMPER 141-GD-0210 OPEN STATUS |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40004 | 3
53 | 141-GD-0210 | 141-GD-0210-ZIC | MOTORIZED FIRE DAMPER 141-GD-0210 CLOSE STATUS |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40004 | 4
54 | 141-GD-0211 | 141-GD-0211-ZIO | MOTORIZED FIRE DAMPER 141-GD-0211 OPEN STATUS |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40004 | 5
55 | 141-GD-0211 | 141-GD-0211-ZIC | MOTORIZED FIRE DAMPER 141-GD-0211 CLOSE STATUS |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40004 | 6
56 | 141-GB-0118 | SWG_HTR_TRP | LVSWITCHGEAR ROOM ROOM HEATER TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40004 | 7
57 | 141-GB-0118 | SWG_HTR_ON | LVSWITCHGEAR HEATER ON/OFF STATUS |  | BOOL | PLC | DCS | OFF | ON | 40004 | 8
58 | 141-GB-0114 | RR_HTR_TRP | RACK ROOM HEATER TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40004 | 9
59 | 141-GB-0114 | RR_HTR_ON | RACK ROOM HEATER ON/OFF STATUS |  | BOOL | PLC | DCS | OFF | ON | 40004 | 10
60 | 141-GB-0115 | BAT_HTR_TRP | BATTERY ROOM HEATER TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40004 | 11
61 | 141-GB-0115 | BAT_HTR_ON | BATTERYROOM HEATER ON/OFF STATUS |  | BOOL | PLC | DCS | OFF | ON | 40004 | 12
62 | - | EMG_STP | HVACP EMERGENCY STOP |  | BOOL | PLC | DCS | NORMAL | ACTIVE | 40004 | 13
63 | - | MUTE_PB | MUTE PUSH BUTTON |  | BOOL | PLC | DCS | OFF | ON | 40004 | 14
64 | - | RST_PB | RESET PUSH BUTTON |  | BOOL | PLC | DCS | OFF | ON | 40004 | 15
65 | - | PSU1&2_HLTHY | POWER SUPPLY 1 & 2 HEALTHY |  | BOOL | PLC | DCS | UNHEALTHY | HEALTHY | 40005 | 0
66 | - | AFS_HLTHY | PANEL AIR FLOW SWITCH HEALTHY |  | BOOL | PLC | DCS | UNHEALTHY | HEALTHY | 40005 | 1
67 | 141-GA-0105A | AHU1_FAN2_RUN | AHU-1 FAN-2 RUN STATUS |  | BOOL | PLC | DCS | STOPPED | RUNNING | 40005 | 2
68 | 141-GA-0105A | AHU1_FAN2_RMT | AHU-1 FAN-2 REMOTE MODE STATUS |  | BOOL | PLC | DCS | LOCAL | REMOTE | 40005 | 3
69 | 141-GA-0105A | AHU1_FAN2_BRK_TRP | AHU-1 FAN-2 BREAKER TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40005 | 4
70 | - | CHLR1-BFV-ZIO | MOTORIZED BUTTER FLY VALVE CHILLER-1 OPEN STATUS |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40005 | 5
71 | - | CHLR1-BFV-ZIC | MOTORIZED BUTTER FLY VALVE CHILLER-1 CLOSE STATUS |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40005 | 6
72 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40005 | 7
73 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40005 | 8
74 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40005 | 9
75 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40005 | 10
76 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40005 | 11
77 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40005 | 12
78 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40005 | 13
79 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40005 | 14
80 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40005 | 15
81 | 141-GC-0105B | CHLR2_RUN | CHILLER-2 UNIT RUN STATUS |  | BOOL | PLC | DCS | STOPPED | RUNNING | 40006 | 0
82 | 141-GC-0105B | CHLR2_TRP | CHILLER-2 UNIT TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40006 | 1
83 | 141-GC-0105B | CHLR2_RMT | CHILLER-2 REMOTE MODE STATUS |  | BOOL | PLC | DCS | LOCAL | REMOTE | 40006 | 2
84 | 141-GC-0105B | CHLR2_BRK_TRP | CHILLER-2 UNIT BREAKER TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40006 | 3
85 | 141-GC-0105B | CHLR2_FS | CHILLER-2 FLOW SWITCH STATUS |  | BOOL | PLC | DCS | NO FLOW | FLOW ON | 40006 | 4
86 | 141-GA-0105B | AHU2_RUN | AHU-2 RUN STATUS |  | BOOL | PLC | DCS | STOPPED | RUNNING | 40006 | 5
87 | 141-GA-0105B | AHU2_TRP | AHU-2 TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40006 | 6
88 | 141-GA-0105B | AHU2_RMT | AHU-2 REMOTE MODE STATUS |  | BOOL | PLC | DCS | LOCAL | REMOTE | 40006 | 7
89 | 141-GA-0105B | AHU2_BRK_TRP | AHU-2 UNIT BREAKER TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40006 | 8
90 | 141-GA-0105B | AHU2_PF_DPS | AHU-2 PRE-FILTER DIFFERENTIAL PRESSURE HIGH |  | BOOL | PLC | DCS | NORMAL | ALARM | 40006 | 9
91 | 141-GA-0105B | AHU2_FF_DPS | AHU-2 FINE-FILTER DIFFERENTIAL PRESSURE HIGH |  | BOOL | PLC | DCS | NORMAL | ALARM | 40006 | 10
92 | 141-GA-0105B | AHU2_AF_DPS | AHU-2 FAN AIR FLOW DIFFERENTIAL PRESSURE |  | BOOL | PLC | DCS | NO FLOW | FLOW ON | 40006 | 11
93 | 141-GK-0103B | BAT_FAN2_RUN | BATTERY ROOM FAN-2 RUN STATUS |  | BOOL | PLC | DCS | STOPPED | RUNNING | 40006 | 12
94 | 141-GK-0103B | BAT_FAN2_TRP | BATTERY ROOM FAN-2 TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40006 | 13
95 | 141-GK-0103B | BAT_FAN2_RMT | BATTERY ROOM FAN-2 REMOTE MODE STATUS |  | BOOL | PLC | DCS | LOCAL | REMOTE | 40006 | 14
96 | 141-GK-0103B | BAT_FAN2_ES | BATTERY ROOM FAN-2 EMERGENCY STOP |  | BOOL | PLC | DCS | NORMAL | ACTIVE | 40006 | 15
97 | 141-GK-0103B | BAT_FAN2_DPS | DIFFERENTIAL PRESSURE ACROSS BATTERY ROOM FAN-2 |  | BOOL | PLC | DCS | NO FLOW | FLOW ON | 40007 | 0
98 | 141-PC-0105B | CHLR2_PMP_RUN | CHILLER-2 WATER PUMP RUN STATUS |  | BOOL | PLC | DCS | STOPPED | RUNNING | 40007 | 1
99 | 141-PC-0105B | CHLR2_PMP_TRP | CHILLER-2 WATER PUMP TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40007 | 2
100 | 141-PC-0105B | CHLR2_PMP_RMT | CHILLER-2 WATER PUMP REMOTE MODE STATUS |  | BOOL | PLC | DCS | LOCAL | REMOTE | 40007 | 3
101 | 141-PC-0105B | CHLR2_PMP_ES | CHILLER-2 WATER PUMP EMERGENCY STOP |  | BOOL | PLC | DCS | NORMAL | ACTIVE | 40007 | 4
102 | - | AHU2-BFV-ZIO | MOTORIZED BUTTER FLY VALVE AHU-2 OPEN STATUS |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40007 | 5
103 | - | AHU2-BFV-ZIC | MOTORIZED BUTTER FLY VALVE AHU-2 CLOSE STATUS |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40007 | 6
104 | 141-GD-0222 | 141-GD-0222-ZIO | MOTORIZED SHUTOFF DAMPER 141-GD-0222 OPEN STATUS |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40007 | 7
105 | 141-GD-0222 | 141-GD-0222-ZIC | MOTORIZED SHUTOFF DAMPER 141-GD-0222 CLOSE STATUS |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40007 | 8
106 | 141-GD-0224 | 141-GD-0224-ZIO | MOTORIZED SHUTOFF DAMPER 141-GD-0224 OPEN STATUS |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40007 | 9
107 | 141-GD-0224 | 141-GD-0224-ZIC | MOTORIZED SHUTOFF DAMPER 141-GD-0224 CLOSE STATUS |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40007 | 10
108 | 141-GD-0227 | 141-GD-0227-ZIO | MOTORIZED SHUTOFF DAMPER 141-GD-0227 OPEN STATUS |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40007 | 11
109 | 141-GD-0227 | 141-GD-0227-ZIC | MOTORIZED SHUTOFF DAMPER 141-GD-0227 CLOSE STATUS |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40007 | 12
110 | 141-GD-0212 | 141-GD-0212-ZIO | MOTORIZED FIRE DAMPER 141-GD-0212 OPEN STATUS |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40007 | 13
111 | 141-GD-0212 | 141-GD-0212-ZIC | MOTORIZED FIRE DAMPER 141-GD-0212 CLOSE STATUS |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40007 | 14
112 | 141-GD-0213 | 141-GD-0213-ZIO | MOTORIZED FIRE DAMPER 141-GD-0213 OPEN STATUS |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40007 | 15
113 | 141-GD-0213 | 141-GD-0213-ZIC | MOTORIZED FIRE DAMPER 141-GD-0213 CLOSE STATUS |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40008 | 0
114 | 141-GD-0214 | 141-GD-0214-ZIO | MOTORIZED FIRE DAMPER 141-GD-0214 OPEN STATUS |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40008 | 1
115 | 141-GD-0214 | 141-GD-0214-ZIC | MOTORIZED FIRE DAMPER 141-GD-0214 CLOSE STATUS |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40008 | 2
116 | 141-GD-0215 | 141-GD-0215-ZIO | MOTORIZED FIRE DAMPER 141-GD-0215 OPEN STATUS |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40008 | 3
117 | 141-GD-0215 | 141-GD-0215-ZIC | MOTORIZED FIRE DAMPER 141-GD-0215 CLOSE STATUS |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40008 | 4
118 | 141-GB-0116 | UPS_HTR_TRP | UPS ROOM HEATER TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40008 | 5
119 | 141-GB-0116 | UPS_HTR_ON | UPS ROOM HEATER ON/OFF STATUS |  | BOOL | PLC | DCS | OFF | ON | 40008 | 6
120 | 141-GB-0117 | TLR_HTR_TRP | TELECOM ROOM HEATER TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40008 | 7
121 | 141-GB-0117 | TLR_HTR_ON | TELECOM HEATER ON/OFF STATUS |  | BOOL | PLC | DCS | OFF | ON | 40008 | 8
122 | - | INC1_ON | MAIN INCOMER-1 ON/OFF STATUS |  | BOOL | PLC | DCS | OPEN | CLOSE | 40008 | 9
123 | - | INC1_TRP | MAIN INCOMER-1 TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40008 | 10
124 | - | INC2_ON | MAIN INCOMER-2 ON/OFF STATUS |  | BOOL | PLC | DCS | OPEN | CLOSE | 40008 | 11
125 | - | INC2_TRP | MAIN INCOMER-2 TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40008 | 12
126 |  | HVAC_SHUT | HVAC SHUTDOWN COMMAND FROM F&G AND ALL DAMPERS CLOSE |  | BOOL | PLC | DCS | NORMAL | SHUTDOWN | 40008 | 13
127 |  | HVAC_RECR | HVAC RECIRCULATION MODE FROM F&G AND AIR INTAKE DAMPER CLOSE |  | BOOL | PLC | DCS | NORMAL | RECIRCUL | 40008 | 14
128 |  | HVAC_H2_HIGH | HVAC HYDROGEN HIGH IN BATTERY ROOM FROM F&G |  | BOOL | PLC | DCS | NORMAL | H2 HIGH | 40008 | 15
129 | 141-GB-0119 | HAVC_HTR_TRP | HVAC ROOM HEATER TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40009 | 0
130 | 141-GB-0119 | HVAC_HTR_ON | HVAC HEATER ON/OFF STATUS |  | BOOL | PLC | DCS | OFF | ON | 40009 | 1
131 | 141-GA-0105B | AHU2_FAN2_RUN | AHU-2 FAN-2 RUN STATUS |  | BOOL | PLC | DCS | STOPPED | RUNNING | 40009 | 2
132 | 141-GA-0105B | AHU2_FAN2_RMT | AHU-2 FAN-2 REMOTE MODE STATUS |  | BOOL | PLC | DCS | LOCAL | REMOTE | 40009 | 3
133 | 141-GA-0105B | AHU2_FAN2_BRK_TRP | AHU-2 FAN-2 BREAKER TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40009 | 4
134 | - | CHLR2-BFV-ZIO | MOTORIZED BUTTER FLY VALVE CHILLER-2 OPEN STATUS |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40009 | 5
135 | - | CHLR2-BFV-ZIC | MOTORIZED BUTTER FLY VALVE CHILLER-1 CLOSE STATUS |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40009 | 6
136 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40009 | 7
137 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40009 | 8
138 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40009 | 9
139 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40009 | 10
140 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40009 | 11
141 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40009 | 12
142 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40009 | 13
143 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40009 | 14
144 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40009 | 15
S.NO | EQUIPMENT TAG | TAG NAME | DESSCRIPTION | MULTIPLICATION FACTOR | DATA TYPE | SIGNAL FROM | SIGNAL TO | RANGE | HIGH SET POINT | MODBUS ADDRESS | BIT
#REF! | 141-DPIT-0201 | DPIT-1 | DIFFERENTIAL PRESSURE FRESH AIR DUCT | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-6 Pa | - | 40020 | -
#REF! | 141-DPIT-0202 | DPIT-2 | DIFFERENTIAL PRESSURE HVAC ROOM | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-6 Pa | - | 40021 | -
#REF! | 141-DPIT-0203 | DPIT-3 | DIFFERENTIAL PRESSURE LV SWT. GR. ROOM | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-6 Pa | - | 40022 | -
#REF! | 141-DPIT-0204 | DPIT-4 | DIFFERENTIAL PRESSURE LV SWT. GR. AIRLOCK ROOM | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-6 Pa | - | 40023 | -
#REF! | 141-TT-0201 | TT-001 | FRESH AIR DUCT TEMPERATURE | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-55 °C | - | 40024 | -
#REF! | 141-TT-0202 | TT-002 | COMMON SUPPLY AIR DUCT TEMPERATURE | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-55 °C | - | 40025 | -
#REF! | 141-TT-0203 | TT-003 | COMMON RETURN AIR DUCT TEMPERATURE | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-55 °C | - | 40026 | -
#REF! | 141-TT-0204 | TT-004 | HVAC ROOM TEMPERATURE | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-55 °C | - | 40027 | -
#REF! | 141-TT-0205 | TT-005 | LV SWT. GR. ROOM TEMPERATURE | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-55 °C | - | 40028 | -
#REF! | 141-HT-0201 | HT-001 | COMMON RETURN AIR DUCT HUMIDITY | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-100 RH | - | 40029 | -
#REF! | 141-HT-0202 | HT-002 | HVAC ROOM HUMIDITY | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-100 RH | - | 40030 | -
#REF! | 141-HT-0203 | HT-003 | LV SWT. GR. ROOM HUMIDITY | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-100 RH | - | 40031 | -
#REF! | 141-HT-0204 | HT-004 | RACK ROOM HUMIDITY | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-100 RH | - | 40032 | -
#REF! | 141-HT-0205 | HT-005 | TELECOM ROOM HUMIDITY | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-100 RH | - | 40033 | -
#REF! | 141-PC-0105A | CHLR1-PMP-SPD-FB | CHILLER-1 WATER PUMP SPEED FEEDBACK | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-50 Hz | - | 40034 | -
#REF! | 141-GD-0225 | 141-GD-0225-FB | MODULATING FRESH AIR DAMPER GD-0225 POSITION FEEDBACK | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-100 % | - | 40035 | -
#REF! | 141-GA-0105A | AHU1-FAN1-SPD-FB | AHU-1 FAN-1 SPEED FEEDBACK | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-50 Hz | - | 40036 | -
#REF! | 141-GA-0105A | AHU1-FAN2-SPD-FB | AHU-1 FAN-2 SPEED FEEDBACK | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-50 Hz | - | 40037 | -
#REF! | AHU-A-TCV | AHU-A-TCV-FB | AHU A 3 WAY TCV POSITION FEEDBACK | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-100 % | - | 40038 | -
#REF! | - |  | SPARE | DIVIDED BY 100 | INTEGER | PLC | DCS | - | - | 40039 | -
#REF! | - |  | SPARE | DIVIDED BY 100 | INTEGER | PLC | DCS | - | - | 40040 | -
#REF! | - |  | SPARE | DIVIDED BY 100 | INTEGER | PLC | DCS | - | - | 40041 | -
#REF! | - |  | SPARE | DIVIDED BY 100 | INTEGER | PLC | DCS | - | - | 40042 | -
#REF! | - |  | SPARE | DIVIDED BY 100 | INTEGER | PLC | DCS | - | - | 40043 | -
#REF! | 141-DPIT-0205 | DPIT-5 | DIFFERENTIAL PRESSURE RACK ROOM | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-6 Pa | - | 40044 | -
#REF! | 141-DPIT-0206 | DPIT-6 | DIFFERENTIAL PRESSURE RACK AIRLOCK ROOM | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-6 Pa | - | 40045 | -
#REF! | 141-DPIT-0207 | DPIT-7 | DIFFERENTIAL PRESSURE TELECOM ROOM | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-6 Pa | - | 40046 | -
#REF! | 141-DPIT-0208 | DPIT-8 | DIFFERENTIAL PRESSURE BATTERY ROOM | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-6 Pa | - | 40047 | -
#REF! | 141-TT-0206 | TT-006 | RACK ROOM TEMPERATURE | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-55 °C | - | 40048 | -
#REF! | 141-TT-0207 | TT-007 | TELECOM ROOM TEMPERATURE | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-55 °C | - | 40049 | -
#REF! | 141-TT-0208 | TT-008 | UPS ROOM TEMPERATURE | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-55 °C | - | 40050 | -
#REF! | 141-TT-0209 | TT-009 | BATTERY ROOM TEMPERATURE | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-55 °C | - | 40051 | -
#REF! | 141-HT-0206 | HT-006 | UPS ROOM HUMIDITY | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-100 RH | - | 40052 | -
#REF! | 141-HT-0207 | HT-007 | BATTERY ROOM HUMIDITY | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-100 RH | - | 40053 | -
#REF! | 141-PC-0105B | CHLR2-PMP-SPD-FB | CHILLER-2 WATER PUMP SPEED FEEDBACK | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-50 Hz | - | 40054 | -
#REF! | 141-GA-0105B | AHU2-FAN1-SPD-FB | AHU-2 FAN-1 SPEED FEEDBACK | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-50 Hz | - | 40055 | -
#REF! | 141-GA-0105B | AHU2-FAN2-SPD-FB | AHU-2 FAN-2 SPEED FEEDBACK | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-50 Hz | - | 40056 | -
#REF! | AHU-A-TCV | AHU-A-TCV-FB | AHU A 3 WAY TCV POSITION FEEDBACK | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-100 % | - | 40057 | -
#REF! | - | - | SPARE | DIVIDED BY 100 | INTEGER | PLC | DCS | - | - | 40058 | -
#REF! | - | - | SPARE | DIVIDED BY 100 | INTEGER | PLC | DCS | - | - | 40059 | -

## INSTRUMENT_LIST
TRANSMITTERS |  | DPS/FS
DPIT-1 | DIFFERENTIAL PRESSURE FRESH AIR DUCT | CHLR1_FS | CHILLER-1 FLOW SWITCH STATUS
DPIT-2 | DIFFERENTIAL PRESSURE HVAC ROOM | CHLR2_FS | CHILLER-1 FLOW SWITCH STATUS
DPIT-3 | DIFFERENTIAL PRESSURE LV SWT. GR. ROOM | AHU1_PF_DPS | AHU-1 PRE-FILTER DIFFERENTIAL PRESSURE HIGH
DPIT-4 | DIFFERENTIAL PRESSURE LV SWT. GR. AIRLOCK ROOM | AHU1_FF_DPS | AHU-1 FINE-FILTER DIFFERENTIAL PRESSURE HIGH
DPIT-5 | DIFFERENTIAL PRESSURE RACK ROOM | AHU1_AF_DPS | AHU-1 FAN AIR FLOW DIFFERENTIAL PRESSURE
DPIT-6 | DIFFERENTIAL PRESSURE RACK AIRLOCK ROOM | AHU2_PF_DPS | AHU-2 PRE-FILTER DIFFERENTIAL PRESSURE HIGH
DPIT-7 | DIFFERENTIAL PRESSURE TELECOM ROOM | AHU2_FF_DPS | AHU-2 FINE-FILTER DIFFERENTIAL PRESSURE HIGH
DPIT-8 | DIFFERENTIAL PRESSURE BATTERY ROOM | AHU2_AF_DPS | AHU-2 FAN AIR FLOW DIFFERENTIAL PRESSURE
TT-001 | FRESH AIR DUCT TEMPERATURE | BAT_FAN1_DPS | DIFFERENTIAL PRESSURE ACROSS BATTERY ROOM FAN-1
TT-002 | COMMON SUPPLY AIR DUCT TEMPERATURE | BAT_FAN2_DPS | DIFFERENTIAL PRESSURE ACROSS BATTERY ROOM FAN-2
TT-003 | COMMON RETURN AIR DUCT TEMPERATURE
TT-004 | HVAC ROOM TEMPERATURE
TT-005 | LV SWT. GR. ROOM TEMPERATURE
TT-006 | RACK ROOM TEMPERATURE
TT-007 | TELECOM ROOM TEMPERATURE
TT-008 | UPS ROOM TEMPERATURE
TT-009 | BATTERY ROOM TEMPERATURE
HT-001 | COMMON RETURN AIR DUCT HUMIDITY
HT-002 | HVAC ROOM HUMIDITY
HT-003 | LV SWT. GR. ROOM HUMIDITY
HT-004 | RACK ROOM HUMIDITY
HT-005 | TELECOM ROOM HUMIDITY
HT-006 | UPS ROOM HUMIDITY
HT-007 | BATTERY ROOM HUMIDITY
QTY | DESCRIPTION | QTY | DESCRIPTION
1 | DPIT - DUCT MOUNTED - OUTSIDE | 2 | FS - CHILLER SPPLY LINE MOUNTED - OUTSIDE
6 | DPIT - WALL MOUNTED - INSIDE THE ROOM | 4 | DPS - AHU OUTSIDE MOUNTED
1 | TT - DUCT MOUNTED - OUTSIDE | 2 | FS - INSIDE AHU MOUNTED
2 | TT -DUCT MOUNTED - INSIDE THE ROOM | 2 | DPS - BATTERY ROOM
5 | TT - WALL MOUNTED - INSIDE THE ROOM
1 | HT -DUCT MOUNTED - INSIDE THE ROOM
5 | HT - WALL MOUNTED - INSIDE THE ROOM
1 | DPIT - WALL MOUNTED - INSIDE THE BAT.ROOM-EX
1 | TT - WALL MOUNTED - INSIDE THE BAT.ROOM-EX
1 | HT - WALL MOUNTED - INSIDE THE BAT.ROOM-EX