## DI
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
OPERATING SHELTER
RUWAIS - U.A.E.
[10 empty] | FACILITY NAME: BOROUGE 4 |  |  |  | COMPANY PROJ. NO. |  | 4700000897
[14 empty] | CONTRACTOR. PROJ. NO. |  | 083118C
|  | OS-HVAC-CP | [7 empty] | DOCUMENT TITLE: OS HVAC PLC System - I/O List REV 4 |  |  |  | SUBCONTR. ID |  | -
Sl. No. | IM Module | I/O Detail |  |  |  |  | FROM | EQUIPMENT TAG | PLC TAG | Description | States |  | PLC Term. | TB GROUP |  | Verified & Signed (Remarks)
|  | Module | Supply | Type | Range | Unit |  |  |  |  | FALSE | TRUE
DIGITAL INPUT
1 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 141-GC-0103A | CHLR1_RUN | CHILLER-1 UNIT RUN STATUS | STOPPED | RUNNING | I0.0 | XDI1-1 | XDI1-2
2 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 141-GC-0103A | CHLR1_TRP | CHILLER-1 UNIT TRIP STATUS | NORMAL | TRIP | I0.1 | XDI1-3 | XDI1-4
3 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 141-GC-0103A | CHLR1_RMT | CHILLER-1 REMOTE MODE STATUS | LOCAL | REMOTE | I0.2 | XDI1-5 | XDI1-6
4 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-001B | 141-GC-0103A | CHLR1_BRK_TRP | CHILLER-1 UNIT BREAKER TRIP STATUS | NORMAL | TRIP | I0.3 | XDI1-7 | XDI1-8
5 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 141-GC-0103A | CHLR1_FS | CHILLER-1 FLOW SWITCH STATUS | NO FLOW | FLOW ON | I0.4 | XDI1-9 | XDI1-10
6 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-001B | 141-GA-0101A | AHU1_FAN1_RUN | AHU-1 FAN-1 RUN STATUS | STOPPED | RUNNING | I0.5 | XDI1-11 | XDI1-12
7 | IM1 | DI1 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I0.6 | XDI1-13 | XDI1-14
8 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-001B | 141-GA-0101A | AHU1_FAN1_RMT | AHU-1 FAN-1 REMOTE MODE STATUS | LOCAL | REMOTE | I0.7 | XDI1-15 | XDI1-16
9 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-001B | 141-GA-0101A | AHU1_FAN1_BRK_TRP | AHU-1 FAN-1 BREAKER TRIP STATUS | NORMAL | TRIP | I1.0 | XDI1-17 | XDI1-18
10 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 141-GA-0101A | AHU1_PF_DPS | AHU-1 PRE-FILTER DIFFERENTIAL PRESSURE HIGH | NORMAL | ALARM | I1.1 | XDI1-19 | XDI1-20
11 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 141-GA-0101A | AHU1_FF_DPS | AHU-1 FINE-FILTER DIFFERENTIAL PRESSURE HIGH | NORMAL | ALARM | I1.2 | XDI1-21 | XDI1-22
12 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 141-GA-0101A | AHU1_AF_DPS | AHU-1 FAN AIR FLOW DIFFERENTIAL PRESSURE | NO FLOW | FLOW ON | I1.3 | XDI1-23 | XDI1-24
13 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-001B | 141-GK-0101A | TLT_FAN1_RUN | TOILET ROOM FAN-1 RUN STATUS | STOPPED | RUNNING | I1.4 | XDI1-25 | XDI1-26
14 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-001B | 141-GK-0101A | TLT_FAN1_TRP | TOILET ROOM FAN-1 TRIP STATUS | NORMAL | TRIP | I1.5 | XDI1-27 | XDI1-28
15 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-001B | 141-GK-0101A | TLT_FAN1_RMT | TOILET ROOM FAN-1 REMOTE MODE STATUS | LOCAL | REMOTE | I1.6 | XDI1-29 | XDI1-30
16 | IM1 | DI1 | 24VDC | VF | - | - | 141-ES-001B | 141-GK-0101A | TLT_FAN1_ES | TOILET ROOM FAN-1 EMERGENCY STOP | NORMAL | ACTIVE | I1.7 | XDI1-31 | XDI1-32
17 | IM1 | DI2 | 24VDC | VF | - | - | FIELD | 141-GK-0101A | TLT_FAN1&2_DPS | DIFFERENTIAL PRESSURE ACROSS TOILET ROOM FAN-1&2 | NO FLOW | FLOW ON | I2.0 | XDI2-1 | XDI2-2
18 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001B | 141-PC-0103A | CHLR1_PMP_RUN | CHILLER-1 WATER PUMP RUN STATUS | STOPPED | RUNNING | I2.1 | XDI2-3 | XDI2-4
19 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001B | 141-PC-0103A | CHLR1_PMP_TRP | CHILLER-1 WATER PUMP TRIP STATUS | NORMAL | TRIP | I2.2 | XDI2-5 | XDI2-6
20 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001B | 141-PC-0103A | CHLR1_PMP_RMT | CHILLER-1 WATER PUMP REMOTE MODE STATUS | LOCAL | REMOTE | I2.3 | XDI2-7 | XDI2-8
21 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001B | 141-PC-0103A | CHLR1_PMP_ES | CHILLER-1 WATER PUMP EMERGENCY STOP | NORMAL | ACTIVE | I2.4 | XDI2-9 | XDI2-10
22 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001B | - | BLD_FAN_RUN | BLEED FAN RUN STATUS | STOPPED | RUNNING | I2.5 | XDI2-11 | XDI2-12
23 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001B | - | BLD_FAN_TRP | BLEED FAN TRIP STATUS | NORMAL | TRIP | I2.6 | XDI2-13 | XDI2-14
24 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001B | - | BLD_FAN_RMT | BLEED FAN REMOTE MODE STATUS | LOCAL | REMOTE | I2.7 | XDI2-15 | XDI2-16
25 | IM1 | DI2 | 24VDC | VF | - | - | 141-ES-001B | - | BLD_FAN_ES | BLEED FAN EMERGENCY STOP | NORMAL | ACTIVE | I3.0 | XDI2-17 | XDI2-18
26 | IM1 | DI2 | 24VDC | VF | - | - | FIELD | - | AHU1-BFV-ZIO | MOTORIZED BUTTER FLY VALVE AHU-1 OPEN STATUS | NOT OPEN | OPEN | I3.1 | XDI2-19 | XDI2-20
27 | IM1 | DI2 | 24VDC | VF | - | - | FIELD | - | AHU1-BFV-ZIC | MOTORIZED BUTTER FLY VALVE AHU-1 CLOSE STATUS | NOT CLOSE | CLOSE | I3.2 | XDI2-21 | XDI2-22
28 | IM1 | DI2 | 24VDC | VF | - | - | FIELD | 141-GD-0331 | 141-GD-0331-ZIO | MOTORIZED SHUTOFF DAMPER 141-GD-0331 OPEN FEEDBACK | NOT OPEN | OPEN | I3.3 | XDI2-23 | XDI2-24
29 | IM1 | DI2 | 24VDC | VF | - | - | FIELD | 141-GD-0331 | 141-GD-0331-ZIC | MOTORIZED SHUTOFF DAMPER 141-GD-0331 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I3.4 | XDI2-25 | XDI2-26
30 | IM1 | DI2 | 24VDC | VF | - | - | FIELD | 141-GD-0332 | 141-GD-0332-ZIO | MOTORIZED SHUTOFF DAMPER 141-GD-0332 OPEN FEEDBACK | NOT OPEN | OPEN | I3.5 | XDI2-27 | XDI2-28
31 | IM1 | DI2 | 24VDC | VF | - | - | FIELD | 141-GD-0332 | 141-GD-0332-ZIC | MOTORIZED SHUTOFF DAMPER 141-GD-0332 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I3.6 | XDI2-29 | XDI2-30
32 | IM1 | DI2 | 24VDC | VF | - | - | FIELD | 141-GD-0336 | 141-GD-0336-ZIO | MOTORIZED SHUTOFF DAMPER 141-GD-0336 OPEN FEEDBACK | NOT OPEN | OPEN | I3.7 | XDI2-31 | XDI2-32
33 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0336 | 141-GD-0336-ZIC | MOTORIZED SHUTOFF DAMPER 141-GD-0336 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I4.0 | XDI3-1 | XDI3-2
34 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0301 | 141-GD-0301-ZIO | MOTORIZED GAS DAMPER 141-GD-0301 OPEN FEEDBACK | NOT OPEN | OPEN | I4.1 | XDI3-3 | XDI3-4
35 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0301 | 141-GD-0301-ZIC | MOTORIZED GAS DAMPER 141-GD-0301 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I4.2 | XDI3-5 | XDI3-6
36 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0302 | 141-GD-0302-ZIO | MOTORIZED GAS DAMPER 141-GD-0302 OPEN FEEDBACK | NOT OPEN | OPEN | I4.3 | XDI3-7 | XDI3-8
37 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0302 | 141-GD-0302-ZIC | MOTORIZED GAS DAMPER 141-GD-0302 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I4.4 | XDI3-9 | XDI3-10
38 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0303 | 141-GD-0303-ZIO | MOTORIZED GAS DAMPER 141-GD-0303 OPEN FEEDBACK | NOT OPEN | OPEN | I4.5 | XDI3-11 | XDI3-12
39 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0303 | 141-GD-0303-ZIC | MOTORIZED GAS DAMPER 141-GD-0303 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I4.6 | XDI3-13 | XDI3-14
40 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0304 | 141-GD-0304-ZIO | MOTORIZED GAS DAMPER 141-GD-0304 OPEN FEEDBACK | NOT OPEN | OPEN | I4.7 | XDI3-15 | XDI3-16
41 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0304 | 141-GD-0304-ZIC | MOTORIZED GAS DAMPER 141-GD-0304 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I5.0 | XDI3-17 | XDI3-18
42 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0305 | 141-GD-0305-ZIO | MOTORIZED GAS DAMPER 141-GD-0305 OPEN FEEDBACK | NOT OPEN | OPEN | I5.1 | XDI3-19 | XDI3-20
43 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0305 | 141-GD-0305-ZIC | MOTORIZED GAS DAMPER 141-GD-0305 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I5.2 | XDI3-21 | XDI3-22
44 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0306 | 141-GD-0306-ZIO | MOTORIZED GAS DAMPER 141-GD-0306 OPEN FEEDBACK | NOT OPEN | OPEN | I5.3 | XDI3-23 | XDI3-24
45 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0306 | 141-GD-0306-ZIC | MOTORIZED GAS DAMPER 141-GD-0306 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I5.4 | XDI3-25 | XDI3-26
46 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0307 | 141-GD-0307-ZIO | MOTORIZED GAS DAMPER 141-GD-0307 OPEN FEEDBACK | NOT OPEN | OPEN | I5.5 | XDI3-27 | XDI3-28
47 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0307 | 141-GD-0307-ZIC | MOTORIZED GAS DAMPER 141-GD-0307 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I5.6 | XDI3-29 | XDI3-30
48 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0308 | 141-GD-0308-ZIO | MOTORIZED GAS DAMPER 141-GD-0308 OPEN FEEDBACK | NOT OPEN | OPEN | I5.7 | XDI3-31 | XDI3-32
49 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0308 | 141-GD-0308-ZIC | MOTORIZED GAS DAMPER 141-GD-0308 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I6.0 | XDI4-1 | XDI4-2
50 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0309 | 141-GD-0309-ZIO | MOTORIZED GAS DAMPER 141-GD-0309 OPEN FEEDBACK | NOT OPEN | OPEN | I6.1 | XDI4-3 | XDI4-4
51 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0309 | 141-GD-0309-ZIC | MOTORIZED GAS DAMPER 141-GD-0309 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I6.2 | XDI4-5 | XDI4-6
52 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0310 | 141-GD-0310-ZIO | MOTORIZED GAS DAMPER 141-GD-0310 OPEN FEEDBACK | NOT OPEN | OPEN | I6.3 | XDI4-7 | XDI4-8
53 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0310 | 141-GD-0310-ZIC | MOTORIZED GAS DAMPER 141-GD-0310 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I6.4 | XDI4-9 | XDI4-10
54 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0311 | 141-GD-0311-ZIO | MOTORIZED GAS DAMPER 141-GD-0311 OPEN FEEDBACK | NOT OPEN | OPEN | I6.5 | XDI4-11 | XDI4-12
55 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0311 | 141-GD-0311-ZIC | MOTORIZED GAS DAMPER 141-GD-0311 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I6.6 | XDI4-13 | XDI4-14
56 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0312 | 141-GD-0312-ZIO | MOTORIZED GAS DAMPER 141-GD-0312 OPEN FEEDBACK | NOT OPEN | OPEN | I6.7 | XDI4-15 | XDI4-16
57 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0312 | 141-GD-0312-ZIC | MOTORIZED GAS DAMPER 141-GD-0312 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I7.0 | XDI4-17 | XDI4-18
58 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0313 | 141-GD-0313-ZIO | MOTORIZED GAS DAMPER 141-GD-0313 OPEN FEEDBACK | NOT OPEN | OPEN | I7.1 | XDI4-19 | XDI4-20
59 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0313 | 141-GD-0313-ZIC | MOTORIZED GAS DAMPER 141-GD-0313 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I7.2 | XDI4-21 | XDI4-22
60 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0314 | 141-GD-0314-ZIO | MOTORIZED GAS DAMPER 141-GD-0314 OPEN FEEDBACK | NOT OPEN | OPEN | I7.3 | XDI4-23 | XDI4-24
61 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0314 | 141-GD-0314-ZIC | MOTORIZED GAS DAMPER 141-GD-0314 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I7.4 | XDI4-25 | XDI4-26
62 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GB-0119 | MW_HTR_TRP | MACHINE WORKSHOP HEATER TRIP STATUS | NORMAL | TRIP | I7.5 | XDI4-27 | XDI4-28
63 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GB-0119 | MW_HTR_ON | MACHINE WORKSHOP HEATER ON/OFF STATUS | OFF | ON | I7.6 | XDI4-29 | XDI4-30
64 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GB-0105 | EIW_HTR_TRP | E&I WORKSHOP HEATER TRIP STATUS | NORMAL | TRIP | I7.7 | XDI4-31 | XDI4-32
65 | IM1 | DI5 | 24VDC | VF | - | - | FIELD | 141-GB-0105 | EIW_HTR_ON | E&I WORKSHOP HEATER ON/OFF STATUS | OFF | ON | I8.0 | XDI5-1 | XDI5-2
66 | IM1 | DI5 | 24VDC | VF | - | - | FIELD | 141-GB-0104 | MTO_HTR_TRP | MAINTENANCE TECHNICIAN OFFICE HEATER TRIP STATUS | NORMAL | TRIP | I8.1 | XDI5-3 | XDI5-4
67 | IM1 | DI5 | 24VDC | VF | - | - | FIELD | 141-GB-0104 | MTO_HTR_ON | MAINTENANCE TECHNICIAN OFFICE HEATER ON/OFF STATUS | OFF | ON | I8.2 | XDI5-5 | XDI5-6
68 | IM1 | DI5 | 24VDC | VF | - | - | FIELD | 141-GB-0103 | TLR_HTR_TRP | TELECOM ROOM HEATER TRIP STATUS | NORMAL | TRIP | I8.3 | XDI5-7 | XDI5-8
69 | IM1 | DI5 | 24VDC | VF | - | - | FIELD | 141-GB-0103 | TLR_HTR_ON | TELECOM ROOM HEATER ON/OFF STATUS | OFF | ON | I8.4 | XDI5-9 | XDI5-10
70 | IM1 | DI5 | 24VDC | VF | - | - | - | - | EMG_STP | HVACP EMERGENCY STOP | NORMAL | ACTIVE | I8.5 | XDI5-11 | XDI5-12
71 | IM1 | DI5 | 24VDC | VF | - | - | - | - | MUTE_PB | MUTE PUSH BUTTON | OFF | ON | I8.6 | XDI5-13 | XDI5-14
72 | IM1 | DI5 | 24VDC | VF | - | - | - | - | RST_PB | RESET PUSH BUTTON | OFF | ON | I8.7 | XDI5-15 | XDI5-16
73 | IM1 | DI5 | 24VDC | VF | - | - | - | - | PSU1&2_HLTHY | POWER SUPPLY 1 & 2 HEALTHY | UNHEALTHY | HEALTHY | I9.0 | XDI5-17 | XDI5-18
74 | IM1 | DI5 | 24VDC | VF | - | - | - | - | AFS_HLTHY | PANEL AIR FLOW SWITCH HEALTHY | UNHEALTHY | HEALTHY | I9.1 | XDI5-19 | XDI5-20
75 | IM1 | DI5 | 24VDC | VF | - | - | 141-ES-001B | - | INC1_ON | MAIN INCOMER-1 ON/OFF STATUS | OPEN | CLOSE | I9.2 | XDI5-21 | XDI5-22
76 | IM1 | DI5 | 24VDC | VF | - | - | 141-ES-001B | - | INC1_TRP | MAIN INCOMER-1 TRIP STATUS | NORMAL | TRIP | I9.3 | XDI5-23 | XDI5-24
77 | IM1 | DI5 | 24VDC | VF | - | - | 141-ES-001B | - | INC2_ON | MAIN INCOMER-2 ON/OFF STATUS | OPEN | CLOSE | I9.4 | XDI5-25 | XDI5-26
78 | IM1 | DI5 | 24VDC | VF | - | - | 141-ES-001B | - | INC2_TRP | MAIN INCOMER-2 TRIP STATUS | NORMAL | TRIP | I9.5 | XDI5-27 | XDI5-28
79 | IM1 | DI5 | 24VDC | VF | - | - | 141-ES-001B | 141-GA-0101A | AHU1_FAN2_RUN | AHU-1 FAN-2 RUN STATUS | STOPPED | RUNNING | I9.6 | XDI5-29 | XDI5-30
80 | IM1 | DI5 | 24VDC | VF | - | - | 141-ES-001B | 141-GA-0101A | AHU1_FAN2_RMT | AHU-1 FAN-2 REMOTE MODE STATUS | LOCAL | REMOTE | I9.7 | XDI5-31 | XDI5-32
81 | IM1 | DI6 | 24VDC | VF | - | - | 141-ES-001B | 141-GA-0101A | AHU1_FAN2_BRK_TRP | AHU-1 FAN-2 BREAKER TRIP STATUS | NORMAL | TRIP | I10.0 | XDI6-1 | XDI6-2
82 | IM1 | DI6 | 24VDC | VF | - | - | - | - | CHLR1-BFV-ZIO | MOTORIZED BUTTER FLY VALVE CHILLER-1 OPEN STATUS | NOT OPEN | OPEN | I10.1 | XDI6-3 | XDI6-4
83 | IM1 | DI6 | 24VDC | VF | - | - | - | - | CHLR1-BFV-ZIC | MOTORIZED BUTTER FLY VALVE CHILLER-1 CLOSE STATUS | NOT CLOSE | CLOSE | I10.2 | XDI6-5 | XDI6-6
84 | IM1 | DI6 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I10.3 | XDI6-7 | XDI6-8
85 | IM1 | DI6 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I10.4 | XDI6-9 | XDI6-10
86 | IM1 | DI6 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I10.5 | XDI6-11 | XDI6-12
87 | IM1 | DI6 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I10.6 | XDI6-13 | XDI6-14
88 | IM1 | DI6 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I10.7 | XDI6-15 | XDI6-16
89 | IM1 | DI6 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I11.0 | XDI6-17 | XDI6-18
90 | IM1 | DI6 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I11.1 | XDI6-19 | XDI6-20
91 | IM1 | DI6 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I11.2 | XDI6-21 | XDI6-22
92 | IM1 | DI6 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I11.3 | XDI6-23 | XDI6-24
93 | IM1 | DI6 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I11.4 | XDI6-25 | XDI6-26
94 | IM1 | DI6 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I11.5 | XDI6-27 | XDI6-28
95 | IM1 | DI6 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I11.6 | XDI6-29 | XDI6-30
96 | IM1 | DI6 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I11.7 | XDI6-31 | XDI6-32
97 | IM2 | DI7 | 24VDC | VF | - | - | FIELD | 141-GC-0103B | CHLR2_RUN | CHILLER-2 UNIT RUN STATUS | STOPPED | RUNNING | I12.0 | XDI7-1 | XDI7-2
98 | IM2 | DI7 | 24VDC | VF | - | - | FIELD | 141-GC-0103B | CHLR2_TRP | CHILLER-2 UNIT TRIP STATUS | NORMAL | TRIP | I12.1 | XDI7-3 | XDI7-4
99 | IM2 | DI7 | 24VDC | VF | - | - | FIELD | 141-GC-0103B | CHLR2_RMT | CHILLER-2 REMOTE MODE STATUS | LOCAL | REMOTE | I12.2 | XDI7-5 | XDI7-6
100 | IM2 | DI7 | 24VDC | VF | - | - | 141-ES-001B | 141-GC-0103B | CHLR2_BRK_TRP | CHILLER-2 UNIT BREAKER TRIP STATUS | NORMAL | TRIP | I12.3 | XDI7-7 | XDI7-8
101 | IM2 | DI7 | 24VDC | VF | - | - | FIELD | 141-GC-0103B | CHLR2_FS | CHILLER-2 FLOW SWITCH STATUS | NO FLOW | FLOW ON | I12.4 | XDI7-9 | XDI7-10
102 | IM2 | DI7 | 24VDC | VF | - | - | 141-ES-001B | 141-GA-0101B | AHU2_FAN1_RUN | AHU-2 FAN-1 RUN STATUS | STOPPED | RUNNING | I12.5 | XDI7-11 | XDI7-12
103 | IM2 | DI7 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I12.6 | XDI7-13 | XDI7-14
104 | IM2 | DI7 | 24VDC | VF | - | - | 141-ES-001B | 141-GA-0101B | AHU2_FAN1_RMT | AHU-2 FAN-1 REMOTE MODE STATUS | LOCAL | REMOTE | I12.7 | XDI7-15 | XDI7-16
1 | IM2 | DI7 | 24VDC | VF | - | - | 141-ES-001B | 141-GA-0101B | AHU2_FAN1_BRK_TRP | AHU-2 FAN-1 UNIT BREAKER TRIP STATUS | NORMAL | TRIP | I13.0 | XDI7-17 | XDI7-18
106 | IM2 | DI7 | 24VDC | VF | - | - | FIELD | 141-GA-0101B | AHU2_PF_DPS | AHU-2 PRE-FILTER DIFFERENTIAL PRESSURE HIGH | NORMAL | ALARM | I13.1 | XDI7-19 | XDI7-20
107 | IM2 | DI7 | 24VDC | VF | - | - | FIELD | 141-GA-0101B | AHU2_FF_DPS | AHU-2 FINE-FILTER DIFFERENTIAL PRESSURE HIGH | NORMAL | ALARM | I13.2 | XDI7-21 | XDI7-22
108 | IM2 | DI7 | 24VDC | VF | - | - | FIELD | 141-GA-0101B | AHU2_AF_DPS | AHU-2 FAN AIR FLOW DIFFERENTIAL PRESSURE | NO FLOW | FLOW ON | I13.3 | XDI7-23 | XDI7-24
109 | IM2 | DI7 | 24VDC | VF | - | - | 141-ES-001B | 141-GK-0101B | TLT_FAN2_RUN | TOILET ROOM FAN-2 RUN STATUS | STOPPED | RUNNING | I13.4 | XDI7-25 | XDI7-26
110 | IM2 | DI7 | 24VDC | VF | - | - | 141-ES-001B | 141-GK-0101B | TLT_FAN2_TRP | TOILET ROOM FAN-2 TRIP STATUS | NORMAL | TRIP | I13.5 | XDI7-27 | XDI7-28
111 | IM2 | DI7 | 24VDC | VF | - | - | 141-ES-001B | 141-GK-0101B | TLT_FAN2_RMT | TOILET ROOM FAN-2 REMOTE MODE STATUS | LOCAL | REMOTE | I13.6 | XDI7-29 | XDI7-30
112 | IM2 | DI7 | 24VDC | VF | - | - | 141-ES-001B | 141-GK-0101B | TLT_FAN2_ES | TOILET ROOM FAN-2 EMERGENCY STOP | NORMAL | ACTIVE | I13.7 | XDI7-31 | XDI7-32
113 | IM2 | DI8 | 24VDC | VF | - | - | 141-ES-001B | 141-PC-0103B | CHLR2_PMP_RUN | CHILLER-2 WATER PUMP RUN STATUS | STOPPED | RUNNING | I14.0 | XDI8-1 | XDI8-2
114 | IM2 | DI8 | 24VDC | VF | - | - | 141-ES-001B | 141-PC-0103B | CHLR2_PMP_TRP | CHILLER-2 WATER PUMP TRIP STATUS | NORMAL | TRIP | I14.1 | XDI8-3 | XDI8-4
115 | IM2 | DI8 | 24VDC | VF | - | - | 141-ES-001B | 141-PC-0103B | CHLR2_PMP_RMT | CHILLER-2 WATER PUMP REMOTE MODE STATUS | LOCAL | REMOTE | I14.2 | XDI8-5 | XDI8-6
116 | IM2 | DI8 | 24VDC | VF | - | - | 141-ES-001B | 141-PC-0103B | CHLR2_PMP_ES | CHILLER-2 WATER PUMP EMERGENCY STOP | NORMAL | ACTIVE | I14.3 | XDI8-7 | XDI8-8
117 | IM2 | DI8 | 24VDC | VF | - | - | FIELD | - | AHU2-BFV-ZIO | MOTORIZED BUTTER FLY VALVE AHU-2 OPEN STATUS | NOT OPEN | OPEN | I14.4 | XDI8-9 | XDI8-10
118 | IM2 | DI8 | 24VDC | VF | - | - | FIELD | - | AHU2-BFV-ZIC | MOTORIZED BUTTER FLY VALVE AHU-2 CLOSE STATUS | NOT CLOSE | CLOSE | I14.5 | XDI8-11 | XDI8-12
119 | IM2 | DI8 | 24VDC | VF | - | - | FIELD | 141-GD-0333 | 141-GD-0333-ZIO | MOTORIZED SHUTOFF DAMPER 141-GD-0333 OPEN FEEDBACK | NOT OPEN | OPEN | I14.6 | XDI8-13 | XDI8-14
120 | IM2 | DI8 | 24VDC | VF | - | - | FIELD | 141-GD-0333 | 141-GD-0333-ZIC | MOTORIZED SHUTOFF DAMPER 141-GD-0333 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I14.7 | XDI8-15 | XDI8-16
121 | IM2 | DI8 | 24VDC | VF | - | - | FIELD | 141-GD-0334 | 141-GD-0334-ZIO | MOTORIZED SHUTOFF DAMPER 141-GD-0334 OPEN FEEDBACK | NOT OPEN | OPEN | I15.0 | XDI8-17 | XDI8-18
122 | IM2 | DI8 | 24VDC | VF | - | - | FIELD | 141-GD-0334 | 141-GD-0334-ZIC | MOTORIZED SHUTOFF DAMPER 141-GD-0334 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I15.1 | XDI8-19 | XDI8-20
123 | IM2 | DI8 | 24VDC | VF | - | - | FIELD | 141-GD-0315 | 141-GD-0315-ZIO | MOTORIZED GAS DAMPER 141-GD-0315 OPEN FEEDBACK | NOT OPEN | OPEN | I15.2 | XDI8-21 | XDI8-22
124 | IM2 | DI8 | 24VDC | VF | - | - | FIELD | 141-GD-0315 | 141-GD-0315-ZIC | MOTORIZED GAS DAMPER 141-GD-0315 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I15.3 | XDI8-23 | XDI8-24
125 | IM2 | DI8 | 24VDC | VF | - | - | FIELD | 141-GD-0316 | 141-GD-0316-ZIO | MOTORIZED GAS DAMPER 141-GD-0316 OPEN FEEDBACK | NOT OPEN | OPEN | I15.4 | XDI8-25 | XDI8-26
126 | IM2 | DI8 | 24VDC | VF | - | - | FIELD | 141-GD-0316 | 141-GD-0316-ZIC | MOTORIZED GAS DAMPER 141-GD-0316 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I15.5 | XDI8-27 | XDI8-28
127 | IM2 | DI8 | 24VDC | VF | - | - | FIELD | 141-GD-0317 | 141-GD-0317-ZIO | MOTORIZED GAS DAMPER 141-GD-0317 OPEN FEEDBACK | NOT OPEN | OPEN | I15.6 | XDI8-29 | XDI8-30
128 | IM2 | DI8 | 24VDC | VF | - | - | FIELD | 141-GD-0317 | 141-GD-0317-ZIC | MOTORIZED GAS DAMPER 141-GD-0317 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I15.7 | XDI8-31 | XDI8-32
129 | IM2 | DI9 | 24VDC | VF | - | - | FIELD | 141-GD-0318 | 141-GD-0318-ZIO | MOTORIZED GAS DAMPER 141-GD-0318 OPEN FEEDBACK | NOT OPEN | OPEN | I16.0 | XDI9-1 | XDI9-2
130 | IM2 | DI9 | 24VDC | VF | - | - | FIELD | 141-GD-0318 | 141-GD-0318-ZIC | MOTORIZED GAS DAMPER 141-GD-0318 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I16.1 | XDI9-3 | XDI9-4
131 | IM2 | DI9 | 24VDC | VF | - | - | FIELD | 141-GD-0319 | 141-GD-0319-ZIO | MOTORIZED GAS DAMPER 141-GD-0319 OPEN FEEDBACK | NOT OPEN | OPEN | I16.2 | XDI9-5 | XDI9-6
132 | IM2 | DI9 | 24VDC | VF | - | - | FIELD | 141-GD-0319 | 141-GD-0319-ZIC | MOTORIZED GAS DAMPER 141-GD-0319 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I16.3 | XDI9-7 | XDI9-8
133 | IM2 | DI9 | 24VDC | VF | - | - | FIELD | 141-GD-0320 | 141-GD-0320-ZIO | MOTORIZED GAS DAMPER 141-GD-0320 OPEN FEEDBACK | NOT OPEN | OPEN | I16.4 | XDI9-9 | XDI9-10
134 | IM2 | DI9 | 24VDC | VF | - | - | FIELD | 141-GD-0320 | 141-GD-0320-ZIC | MOTORIZED GAS DAMPER 141-GD-0320 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I16.5 | XDI9-11 | XDI9-12
135 | IM2 | DI9 | 24VDC | VF | - | - | FIELD | 141-GD-0321 | 141-GD-0321-ZIO | MOTORIZED GAS DAMPER 141-GD-0321 OPEN FEEDBACK | NOT OPEN | OPEN | I16.6 | XDI9-13 | XDI9-14
136 | IM2 | DI9 | 24VDC | VF | - | - | FIELD | 141-GD-0321 | 141-GD-0321-ZIC | MOTORIZED GAS DAMPER 141-GD-0321 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I16.7 | XDI9-15 | XDI9-16
137 | IM2 | DI9 | 24VDC | VF | - | - | FIELD | 141-GD-0322 | 141-GD-0322-ZIO | MOTORIZED GAS DAMPER 141-GD-0322 OPEN FEEDBACK | NOT OPEN | OPEN | I17.0 | XDI9-17 | XDI9-18
138 | IM2 | DI9 | 24VDC | VF | - | - | FIELD | 141-GD-0322 | 141-GD-0322-ZIC | MOTORIZED GAS DAMPER 141-GD-0322 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I17.1 | XDI9-19 | XDI9-20
139 | IM2 | DI9 | 24VDC | VF | - | - | FIELD | 141-GD-0323 | 141-GD-0323-ZIO | MOTORIZED GAS DAMPER 141-GD-0323 OPEN FEEDBACK | NOT OPEN | OPEN | I17.2 | XDI9-21 | XDI9-22
140 | IM2 | DI9 | 24VDC | VF | - | - | FIELD | 141-GD-0323 | 141-GD-0323-ZIC | MOTORIZED GAS DAMPER 141-GD-0323 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I17.3 | XDI9-23 | XDI9-24
141 | IM2 | DI9 | 24VDC | VF | - | - | FIELD | 141-GD-0324 | 141-GD-0324-ZIO | MOTORIZED GAS DAMPER 141-GD-0324 OPEN FEEDBACK | NOT OPEN | OPEN | I17.4 | XDI9-25 | XDI9-26
142 | IM2 | DI9 | 24VDC | VF | - | - | FIELD | 141-GD-0324 | 141-GD-0324-ZIC | MOTORIZED GAS DAMPER 141-GD-0324 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I17.5 | XDI9-27 | XDI9-28
143 | IM2 | DI9 | 24VDC | VF | - | - | FIELD | 141-GD-0325 | 141-GD-0325-ZIO | MOTORIZED GAS DAMPER 141-GD-0325 OPEN FEEDBACK | NOT OPEN | OPEN | I17.6 | XDI9-29 | XDI9-30
144 | IM2 | DI9 | 24VDC | VF | - | - | FIELD | 141-GD-0325 | 141-GD-0325-ZIC | MOTORIZED GAS DAMPER 141-GD-0325 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I17.7 | XDI9-31 | XDI9-32
145 | IM2 | DI10 | 24VDC | VF | - | - | FIELD | 141-GD-0326 | 141-GD-0326-ZIO | MOTORIZED GAS DAMPER 141-GD-0326 OPEN FEEDBACK | NOT OPEN | OPEN | I18.0 | XDI10-1 | XDI10-2
146 | IM2 | DI10 | 24VDC | VF | - | - | FIELD | 141-GD-0326 | 141-GD-0326-ZIC | MOTORIZED GAS DAMPER 141-GD-0326 CLOSE FEEDBACK | NOT CLOSE | CLOSE | I18.1 | XDI10-3 | XDI10-4
147 | IM2 | DI10 | 24VDC | VF | - | - | FIELD | 141-GB-0101 | MSU_HTR_TRP | MAINTENANCE SUPERVISOR OFFICE HEATER TRIP STATUS | NORMAL | TRIP | I18.2 | XDI10-5 | XDI10-6
148 | IM2 | DI10 | 24VDC | VF | - | - | FIELD | 141-GB-0101 | MSU_HTR_ON | MAINTENANCE SUPERVISOR OFFICE HEATER ON/OFF STATUS | OFF | ON | I18.3 | XDI10-7 | XDI10-8
149 | IM2 | DI10 | 24VDC | VF | - | - | FIELD | 141-GB-0102 | EUO_HTR_TRP | EU OPERATORS OFFICE HEATER TRIP STATUS | NORMAL | TRIP | I18.4 | XDI10-9 | XDI10-10
150 | IM2 | DI10 | 24VDC | VF | - | - | FIELD | 141-GB-0102 | EUO_HTR_ON | EU OPERATORS OFFICE HEATER ON/OFF STATUS | OFF | ON | I18.5 | XDI10-11 | XDI10-12
151 | IM2 | DI10 | 24VDC | VF | - | - | FIELD | 141-GB-0106 | TR_HTR_TRP | TEA ROOM HEATER TRIP STATUS | NORMAL | TRIP | I18.6 | XDI10-13 | XDI10-14
152 | IM2 | DI10 | 24VDC | VF | - | - | FIELD | 141-GB-0106 | TR_HTR_ON | TEA ROOM HEATER ON/OFF STATUS | OFF | ON | I18.7 | XDI10-15 | XDI10-16
153 | IM2 | DI10 | 24VDC | VF | - | - | LFCP | - | HVAC_SHUT | HVAC SHUTDOWN COMMAND FROM F&G AND ALL DAMPERS CLOSE | NORMAL | SHUTDOWN | I19.0 | XDI10-17 | XDI10-18
154 | IM2 | DI10 | 24VDC | VF | - | - | LFCP | - | HVAC_RECR | HVAC RECIRCULATION MODE FROM F&G AND AIR INTAKE DAMPER CLOSE | NORMAL | RECIRCUL | I19.1 | XDI10-19 | XDI10-20
155 | IM2 | DI10 | 24VDC | VF | - | - | LFCP | - | HVAC_H2_HIGH | HVAC HYDROGEN HIGH IN TOILET ROOM FROM F&G | NORMAL | H2 HIGH | I19.2 | XDI10-21 | XDI10-22
156 | IM2 | DI10 | 24VDC | VF | - | - | FIELD | 141-GB-0120 | HVAC_RM_HTR_TRP | HVAC ROOM HEATER TRIP STATUS | NORMAL | TRIP | I19.3 | XDI10-23 | XDI10-24
157 | IM2 | DI10 | 24VDC | VF | - | - | FIELD | 141-GB-0120 | HVAC_RM_HTR_ON | HVAC ROOM HEATER ON/OFF STATUS | OFF | ON | I19.4 | XDI10-25 | XDI10-26
158 | IM2 | DI10 | 24VDC | VF | - | - | 141-ES-001B | 141-GA-0101B | AHU2_FAN2_RUN | AHU-2 FAN-2 RUN STATUS | STOPPED | RUNNING | I19.5 | XDI10-27 | XDI10-28
159 | IM2 | DI10 | 24VDC | VF | - | - | 141-ES-001B | 141-GA-0101B | AHU2_FAN2_RMT | AHU-2 FAN-2 REMOTE MODE STATUS | LOCAL | REMOTE | I19.6 | XDI10-29 | XDI10-30
160 | IM2 | DI10 | 24VDC | VF | - | - | 141-ES-001B | 141-GA-0101B | AHU2_FAN2_BRK_TRP | AHU-2 FAN-2 BREAKER TRIP STATUS | NORMAL | TRIP | I19.7 | XDI10-31 | XDI10-32
161 | IM2 | DI11 | 24VDC | VF | - | - | - | - | CHLR2-BFV-ZIO | MOTORIZED BUTTER FLY VALVE CHILLER-2 OPEN STATUS | NOT OPEN | OPEN | I20.0 | XDI11-1 | XDI11-2
162 | IM2 | DI11 | 24VDC | VF | - | - | - | - | CHLR2-BFV-ZIC | MOTORIZED BUTTER FLY VALVE CHILLER-1 CLOSE STATUS | NOT CLOSE | CLOSE | I20.1 | XDI11-3 | XDI11-4
163 | IM2 | DI11 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I20.2 | XDI11-5 | XDI11-6
164 | IM2 | DI11 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I20.3 | XDI11-7 | XDI11-8
165 | IM2 | DI11 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I20.4 | XDI11-9 | XDI11-10
166 | IM2 | DI11 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I20.5 | XDI11-11 | XDI11-12
167 | IM2 | DI11 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I20.6 | XDI11-13 | XDI11-14
168 | IM2 | DI11 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I20.7 | XDI11-15 | XDI11-16
169 | IM2 | DI11 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I21.0 | XDI11-17 | XDI11-18
170 | IM2 | DI11 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I21.1 | XDI11-19 | XDI11-20
171 | IM2 | DI11 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I21.2 | XDI11-21 | XDI11-22
172 | IM2 | DI11 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I21.3 | XDI11-23 | XDI11-24
173 | IM2 | DI11 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I21.4 | XDI11-25 | XDI11-26
174 | IM2 | DI11 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I21.5 | XDI11-27 | XDI11-28
175 | IM2 | DI11 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I21.6 | XDI11-29 | XDI11-30
176 | IM2 | DI11 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | I21.7 | XDI11-31 | XDI11-32

## DO
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
OPERATING SHELTER
RUWAIS - U.A.E.
[10 empty] | FACILITY NAME: BOROUGE 4 |  |  |  | COMPANY PROJ. NO. |  | 4700000897
[14 empty] | CONTRACTOR. PROJ. NO. |  | 083118C
|  | OS-HVAC-CP | [7 empty] | DOCUMENT TITLE: OS HVAC PLC System - I/O List REV 4 |  |  |  | SUBCONTR. ID |  | -
Sl. No. | IM Module | I/O Detail |  |  |  |  | TO | EQUIPMENT TAG | PLC TAG | Description | STATES |  | PLC Term. | TB GROUP |  | Verified & Signed
|  | Module | Supply | Type | Range | Unit |  |  |  |  | FALSE | TRUE
DIGITAL OUTPUT
1 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001B | 141-GC-0103A | CHLR1_CMD | CHILLER-1 START/STOP COMMAND | STOP | START | Q0.0 | XDO1-1 | XDO1-2
2 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001B | 141-GC-0103A | CHLR1_INTL_CMD | CHILLER-1 PUMP INTERLOCK COMMAND | OFF | ON | Q0.1 | XDO1-3 | XDO1-4
3 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001B | 141-GC-0103A | CHLR1_DL_CMD | CHILLER-1 DEMAND LIMIT COMMAND | OFF | ON | Q0.2 | XDO1-5 | XDO1-6
4 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001B | 141-GA-0101A | AHU1_FAN1_CMD | AHU-1 FAN-1 START/STOP COMMAND | STOP | START | Q0.3 | XDO1-7 | XDO1-8
5 | IM1 | DO1 | 24VDC | 240V | - | - | FIELD | - | AHU1_MBFV_OPN | AHU-1 MOTORIZED BUTTER FLY VALVE OPEN COMMAND | NOT OPEN | OPEN | Q0.4 | XDO1-9 | XDO1-10
6 | IM1 | DO1 | 24VDC | 240V | - | - | FIELD | - | AHU1_MBFV_CLS | AHU-1 MOTORIZED BUTTER FLY VALVE CLOSE COMMAND | NOT CLOSE | CLOSE | Q0.5 | XDO1-11 | XDO1-12
7 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001B | 141-GK-0101A | TLT_FAN1_CMD | TOILET ROOM EXHAUST FAN-1 START/STOP COMMAND | STOP | START | Q0.6 | XDO1-13 | XDO1-14
8 | IM1 | DO1 | 24VDC | VF | - | - | 141-ES-001B | 141-PC-0103A | CHLR1_PMP_CMD | CHILLER-1 WATER PUMP START/STOP COMMAND | STOP | START | Q0.7 | XDO1-15 | XDO1-16
9 | IM1 | DO1 | 24VDC | 24AC | - | - | FIELD | 141-GD-0331 | 141-GD-0331-CMD | MOTORIZED SHUTOFF DAMPER 141-GD-0331 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q1.0 | XDO1-17 | XDO1-18
10 | IM1 | DO1 | 24VDC | 24AC | - | - | FIELD | 141-GD-0332 | 141-GD-0332-CMD | MOTORIZED SHUTOFF DAMPER 141-GD-0332 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q1.1 | XDO1-19 | XDO1-20
11 | IM1 | DO1 | 24VDC | 24AC | - | - | FIELD | 141-GD-0301 | 141-GD-0301-CMD | MOTORIZED GAS DAMPER 141-GD-0301 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q1.2 | XDO1-21 | XDO1-22
12 | IM1 | DO1 | 24VDC | 24AC | - | - | FIELD | 141-GD-0302 | 141-GD-0302-CMD | MOTORIZED FIRE DAMPER 141-GD-0302 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q1.3 | XDO1-23 | XDO1-24
13 | IM1 | DO1 | 24VDC | 24AC | - | - | FIELD | 141-GD-0303 | 141-GD-0303-CMD | MOTORIZED FIRE DAMPER 141-GD-0303 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q1.4 | XDO1-25 | XDO1-26
14 | IM1 | DO1 | 24VDC | 24AC | - | - | FIELD | 141-GD-0304 | 141-GD-0304-CMD | MOTORIZED FIRE DAMPER 141-GD-0304 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q1.5 | XDO1-27 | XDO1-28
15 | IM1 | DO1 | 24VDC | 24AC | - | - | FIELD | 141-GD-0305 | 141-GD-0305-CMD | MOTORIZED FIRE DAMPER 141-GD-0305 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q1.6 | XDO1-29 | XDO1-30
16 | IM1 | DO1 | 24VDC | 24AC | - | - | FIELD | 141-GD-0306 | 141-GD-0306-CMD | MOTORIZED FIRE DAMPER 141-GD-0306 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q1.7 | XDO1-31 | XDO1-32
17 | IM1 | DO2 | 24VDC | 24AC | - | - | FIELD | 141-GD-0307 | 141-GD-0307-CMD | MOTORIZED FIRE DAMPER 141-GD-0307 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q2.0 | XDO2-1 | XDO2-2
18 | IM1 | DO2 | 24VDC | 24AC | - | - | FIELD | 141-GD-0308 | 141-GD-0308-CMD | MOTORIZED FIRE DAMPER 141-GD-0308 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q2.1 | XDO2-3 | XDO2-4
19 | IM1 | DO2 | 24VDC | 24AC | - | - | FIELD | 141-GD-0309 | 141-GD-0309-CMD | MOTORIZED FIRE DAMPER 141-GD-0309 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q2.2 | XDO2-5 | XDO2-6
20 | IM1 | DO2 | 24VDC | 24AC | - | - | FIELD | 141-GD-0310 | 141-GD-0310-CMD | MOTORIZED FIRE DAMPER 141-GD-0310 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q2.3 | XDO2-7 | XDO2-8
21 | IM1 | DO2 | 24VDC | 24AC | - | - | FIELD | 141-GD-0311 | 141-GD-0311-CMD | MOTORIZED FIRE DAMPER 141-GD-0311 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q2.4 | XDO2-9 | XDO2-10
22 | IM1 | DO2 | 24VDC | 24AC | - | - | FIELD | 141-GD-0312 | 141-GD-0312-CMD | MOTORIZED FIRE DAMPER 141-GD-0312 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q2.5 | XDO2-11 | XDO2-12
23 | IM1 | DO2 | 24VDC | 24AC | - | - | FIELD | 141-GD-0313 | 141-GD-0313-CMD | MOTORIZED FIRE DAMPER 141-GD-0313 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q2.6 | XDO2-13 | XDO2-14
24 | IM1 | DO2 | 24VDC | 24AC | - | - | FIELD | 141-GD-0314 | 141-GD-0314-CMD | MOTORIZED FIRE DAMPER 141-GD-0314 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q2.7 | XDO2-15 | XDO2-16
25 | IM1 | DO2 | 24VDC | 24AC | - | - | FIELD | 141-GD-0315 | 141-GD-0315-CMD | MOTORIZED FIRE DAMPER 141-GD-0315 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.0 | XDO2-17 | XDO2-18
26 | IM1 | DO2 | 24VDC | VF | - | - | 141-ES-001B | - | BLEED_CMD | BLEED FAN START/STOP COMMAND | STOP | START | Q3.1 | XDO2-19 | XDO2-20
27 | IM1 | DO2 | 24VDC | VF | - | - | 141-ES-001B | 141-GA-0101A | AHU1_FAN2_CMD | AHU-1 FAN-2 START/STOP COMMAND | STOP | START | Q3.2 | XDO2-21 | XDO2-22
28 | IM1 | DO2 | 24VDC | VF | - | - | - | - | CHLR1_MBFV_OPN | CHILLER-1 MOTORIZED BUTTER FLY VALVE OPEN COMMAND | NOT OPEN | OPEN | Q3.3 | XDO2-23 | XDO2-24
29 | IM1 | DO2 | 24VDC | VF | - | - | - | - | CHLR1_MBFV_CLS | CHILLER-1 MOTORIZED BUTTER FLY VALVE CLOSE COMMAND | NOT CLOSE | CLOSE | Q3.4 | XDO2-25 | XDO2-26
30 | IM1 | DO2 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | Q3.5 | XDO2-27 | XDO2-28
31 | IM1 | DO2 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | Q3.6 | XDO2-29 | XDO2-30
32 | IM1 | DO2 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | Q3.7 | XDO2-31 | XDO2-32
33 | IM2 | DO3 | 24VDC | VF | - | - | 141-ES-001B | 141-GC-0103B | CHLR2_CMD | CHILLER-2 START/STOP COMMAND | STOP | START | Q4.0 | XDO3-1 | XDO3-2
34 | IM2 | DO3 | 24VDC | VF | - | - | 141-ES-001B | 141-GC-0103B | CHLR2_INTL_CMD | CHILLER-2 PUMP INTERLOCK COMMAND | OFF | ON | Q4.1 | XDO3-3 | XDO3-4
35 | IM2 | DO3 | 24VDC | VF | - | - | 141-ES-001B | 141-GC-0103B | CHLR2_DL_CMD | CHILLER-2 DEMAND LIMIT COMMAND | OFF | ON | Q4.2 | XDO3-5 | XDO3-6
36 | IM2 | DO3 | 24VDC | VF | - | - | 141-ES-001B | 141-GA-0101B | AHU2_FAN1_CMD | AHU-2 FAN-1 START/STOP COMMAND | STOP | START | Q4.3 | XDO3-7 | XDO3-8
37 | IM2 | DO3 | 24VDC | 240V | - | - | FIELD | - | AHU2_MBFV_OPN | AHU-2 MOTORIZED BUTTER FLY VALVE OPEN COMMAND | NOT OPEN | OPEN | Q4.4 | XDO3-9 | XDO3-10
38 | IM2 | DO3 | 24VDC | 240V | - | - | FIELD | - | AHU2_MBFV_CLS | AHU-2 MOTORIZED BUTTER FLY VALVE CLOSE COMMAND | NOT CLOSE | CLOSE | Q4.5 | XDO3-11 | XDO3-12
39 | IM2 | DO3 | 24VDC | VF | - | - | 141-ES-001B | 141-GK-0101B | TLT_FAN2_CMD | TOILET ROOM EXHAUST FAN-2 START/STOP COMMAND | STOP | START | Q4.6 | XDO3-13 | XDO3-14
40 | IM2 | DO3 | 24VDC | VF | - | - | 141-ES-001B | 141-PC-0103B | CHLR2_PMP_CMD | CHILLER-2 WATER PUMP START/STOP COMMAND | STOP | START | Q4.7 | XDO3-15 | XDO3-16
41 | IM2 | DO3 | 24VDC | 24AC | - | - | FIELD | 141-GD-0333 | 141-GD-0333-CMD | MOTORIZED SHUTOFF DAMPER 141-GD-0333 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q5.0 | XDO3-17 | XDO3-18
42 | IM2 | DO3 | 24VDC | 24AC | - | - | FIELD | 141-GD-0334 | 141-GD-0334-CMD | MOTORIZED SHUTOFF DAMPER 141-GD-0334 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q5.1 | XDO3-19 | XDO3-20
43 | IM2 | DO3 | 24VDC | 24AC | - | - | FIELD | 141-GD-0336 | 141-GD-0336-CMD | MOTORIZED GAS DAMPER 141-GD-0336 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q5.2 | XDO3-21 | XDO3-22
44 | IM2 | DO3 | 24VDC | 24AC | - | - | FIELD | 141-GD-0316 | 141-GD-0316-CMD | MOTORIZED FIRE DAMPER 141-GD-0316 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q5.3 | XDO3-23 | XDO3-24
45 | IM2 | DO3 | 24VDC | 24AC | - | - | FIELD | 141-GD-0317 | 141-GD-0317-CMD | MOTORIZED FIRE DAMPER 141-GD-0317 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q5.4 | XDO3-25 | XDO3-26
46 | IM2 | DO3 | 24VDC | 24AC | - | - | FIELD | 141-GD-0318 | 141-GD-0318-CMD | MOTORIZED FIRE DAMPER 141-GD-0318 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q5.5 | XDO3-27 | XDO3-28
47 | IM2 | DO3 | 24VDC | 24AC | - | - | FIELD | 141-GD-0319 | 141-GD-0319-CMD | MOTORIZED FIRE DAMPER 141-GD-0319 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q5.6 | XDO3-29 | XDO3-30
48 | IM2 | DO3 | 24VDC | 24AC | - | - | FIELD | 141-GD-0320 | 141-GD-0320-CMD | MOTORIZED FIRE DAMPER 141-GD-0320 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q5.7 | XDO3-31 | XDO3-32
49 | IM2 | DO4 | 24VDC | 24AC | - | - | FIELD | 141-GD-0321 | 141-GD-0321-CMD | MOTORIZED FIRE DAMPER 141-GD-0321 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q6.0 | XDO4-1 | XDO4-2
50 | IM2 | DO4 | 24VDC | 24AC | - | - | FIELD | 141-GD-0322 | 141-GD-0322-CMD | MOTORIZED FIRE DAMPER 141-GD-0322 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q6.1 | XDO4-3 | XDO4-4
51 | IM2 | DO4 | 24VDC | 24AC | - | - | FIELD | 141-GD-0323 | 141-GD-0323-CMD | MOTORIZED FIRE DAMPER 141-GD-0323 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q6.2 | XDO4-5 | XDO4-6
52 | IM2 | DO4 | 24VDC | 24AC | - | - | FIELD | 141-GD-0324 | 141-GD-0324-CMD | MOTORIZED FIRE DAMPER 141-GD-0324 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q6.3 | XDO4-7 | XDO4-8
53 | IM2 | DO4 | 24VDC | 24AC | - | - | FIELD | 141-GD-0325 | 141-GD-0325-CMD | MOTORIZED FIRE DAMPER 141-GD-0325 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q6.4 | XDO4-9 | XDO4-10
54 | IM2 | DO4 | 24VDC | 24AC | - | - | FIELD | 141-GD-0326 | 141-GD-0326-CMD | MOTORIZED FIRE DAMPER 141-GD-0326 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q6.5 | XDO4-11 | XDO4-12
55 | IM2 | DO4 | 24VDC | VF | - | - | F&G | - | HVAC_SHUT_FG | HVAC SHUTDOWN/DAMPER CLOSE FEEDBACK TO F&G | OFF | ON | Q6.6 | XDO4-13 | XDO4-14
56 | IM2 | DO4 | 24VDC | VF | - | - | F&G | - | HVAC_RECIR_FG | RECIRCULATION/DAMPER CLOSE FEEDBACK TO F&G | OFF | ON | Q6.7 | XDO4-15 | XDO4-16
57 | IM2 | DO4 | 24VDC | 24VDC | - | - | 141-ES-001A | - | BUZZ_ON | BUZZER ON COMMAND | OFF | ON | Q7.0 | XDO4-17 | XDO4-18
58 | IM2 | DO4 | 24VDC | VF | - | - | 141-ES-001B | 141-GA-0101B | AHU2_FAN2_CMD | AHU-2 FAN-2 START/STOP COMMAND | STOP | START | Q7.1 | XDO4-19 | XDO4-20
59 | IM2 | DO4 | 24VDC | VF | - | - | - | - | CHLR2_MBFV_OPN | CHILLER-2 MOTORIZED BUTTER FLY VALVE OPEN COMMAND | NOT OPEN | OPEN | Q7.2 | XDO4-21 | XDO4-22
60 | IM2 | DO4 | 24VDC | VF | - | - | - | - | CHLR2_MBFV_CLS | CHILLER-2 MOTORIZED BUTTER FLY VALVE CLOSE COMMAND | NOT CLOSE | CLOSE | Q7.3 | XDO4-23 | XDO4-24
61 | IM2 | DO4 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | Q7.4 | XDO4-25 | XDO4-26
62 | IM2 | DO4 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | Q7.5 | XDO4-27 | XDO4-28
63 | IM2 | DO4 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | Q7.6 | XDO4-29 | XDO4-30
64 | IM2 | DO4 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | Q7.7 | XDO4-31 | XDO4-32

## AI
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
OPERATING SHELTER
RUWAIS - U.A.E.
[10 empty] | FACILITY NAME: BOROUGE 4 | [5 empty] | COMPANY PROJ. NO. |  | 4700000897
[16 empty] | CONTRACTOR. PROJ. NO. |  | 083118C
| OS-HVAC-CP | [8 empty] | DOCUMENT TITLE: OS HVAC PLC System - I/O List REV 4 | [5 empty] | SUBCONTR. ID |  | -
Sl. No. | IM Module | I/O Detail |  |  |  |  | FROM | EQUIPMENT TAG | PLC TAG | Description | Alarm Setpoints |  |  |  | PLC Term. | TB GROUP |  | Verified & Signed
|  | Module | Supply | Type | Range | Unit |  |  |  |  | LL | L | H | HH
ANALOGUE INPUT
1 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | 141-DPIT-0001 | DPIT-1 | DIFFERENTIAL PRESSURE FRESH AIR DUCT | - | 1 | 5 | - | I0+/I0- | XAI1-1 | XAI1-2
2 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | 141-DPIT-0002 | DPIT-2 | DIFFERENTIAL PRESSURE HVAC ROOM | - | 1 | 5 | - | I1+/I1- | XAI1-3 | XAI1-4
3 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | 141-DPIT-0003 | DPIT-3 | DIFFERENTIAL PRESSURE EQUIPMENT TOOL ROOM | - | 1 | 5 | - | I2+/I2- | XAI1-5 | XAI1-6
4 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | 141-DPIT-0004 | DPIT-4 | DIFFERENTIAL PRESSURE E&I WORKSHOP AIRLOCK | - | 1 | 5 | - | I3+/I3- | XAI1-7 | XAI1-8
5 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | 141-DPIT-0005 | DPIT-5 | DIFFERENTIAL PRESSURE MAINTENANCE SUPERVISOR OFFICE | - | 1 | 5 | - | I4+/I4- | XAI1-9 | XAI1-10
6 | IM1 | AI1 | 24VDC | Sink | 0-55 | °C | FIELD | 141-TT-0001 | TT-001 | FRESH AIR DUCT TEMPERATURE | - | 20 | 30 | - | I5+/I5- | XAI1-11 | XAI1-12
7 | IM1 | AI1 | 24VDC | Sink | 0-55 | °C | FIELD | 141-TT-0002 | TT-002 | COMMON SUPPLY AIR DUCT TEMPERATURE | - | 20 | 30 | - | I6+/I6- | XAI1-13 | XAI1-14
8 | IM1 | AI1 | 24VDC | Sink | 0-55 | °C | FIELD | 141-TT-0003 | TT-003 | COMMON RETURN AIR DUCT TEMPERATURE | - | 20 | 30 | - | I7+/I7- | XAI1-15 | XAI1-16
9 | IM1 | AI2 | 24VDC | Sink | 0-55 | °C | FIELD | 141-TT-0004 | TT-004 | HVAC ROOM TEMPERATURE | - | 20 | 30 | - | I0+/I0- | XAI2-1 | XAI2-2
10 | IM1 | AI2 | 24VDC | Sink | 0-55 | °C | FIELD | 141-TT-0005 | TT-005 | EQUIPMENT TOOL ROOM TEMPERATURE | - | 20 | 30 | - | I1+/I1- | XAI2-3 | XAI2-4
11 | IM1 | AI2 | 24VDC | Sink | 0-55 | °C | FIELD | 141-TT-0006 | TT-006 | MACHINE WORKSHOP TEMPERATURE | - | 20 | 30 | - | I2+/I2- | XAI2-5 | XAI2-6
12 | IM1 | AI2 | 24VDC | Sink | 0-100 | RH | FIELD | 141-MT-0001 | MT-001 | COMMON RETURN AIR DUCT HUMIDITY | - | 30 | 60 | - | I3+/I3- | XAI2-7 | XAI2-8
13 | IM1 | AI2 | 24VDC | Sink | 0-100 | RH | FIELD | 141-MT-0002 | MT-002 | HVAC ROOM HUMIDITY | - | 30 | 60 | - | I4+/I4- | XAI2-9 | XAI2-10
14 | IM1 | AI2 | 24VDC | Sink | 0-100 | RH | FIELD | 141-MT-0003 | MT-003 | EQUIPMENT TOOL ROOM HUMIDITY | - | 30 | 60 | - | I5+/I5- | XAI2-11 | XAI2-12
15 | IM1 | AI2 | 24VDC | Sink | 0-100 | RH | FIELD | 141-MT-0004 | MT-004 | MACHANICAL WORKSHOP HUMIDITY | - | 30 | 60 | - | I6+/I6- | XAI2-13 | XAI2-14
16 | IM1 | AI2 | 24VDC | Sink | 0-100 | RH | FIELD | 141-MT-0005 | MT-005 | E&I WORKSHOP HUMIDITY | - | 30 | 60 | - | I7+/I7- | XAI2-15 | XAI2-16
17 | IM1 | AI3 | 24VDC | Sink | 0-50 | HZ | 141-ES-001B | 141-PC-0103A | CHLR1-PMP-SPD-FB | CHILLER-1 WATER PUMP SPEED FEEDBACK | - | - | - | - | I0+/I0- | XAI3-1 | XAI3-2
18 | IM1 | AI3 | 24VDC | Sink | - | - | FIELD | 141-GD-0335 | 141-GD-0335-FB | MODULATING FRESH AIR DAMPER MD-0335 POSITION FEEDBACK | - | - | - | - | I1+/I1- | XAI3-3 | XAI3-4
19 | IM1 | AI3 | 24VDC | Sink | 0-50 | HZ | 141-ES-001B | 141-GA-0101A | AHU1-FAN1-SPD-FB | AHU-1 FAN-1 SPEED FEEDBACK | - | - | - | - | I2+/I2- | XAI3-5 | XAI3-6
20 | IM1 | AI3 | 24VDC | Sink | 0-50 | HZ | 141-ES-001B | 141-GA-0101A | AHU1-FAN2-SPD-FB | AHU-1 FAN-2 SPEED FEEDBACK | - | - | - | - | I3+/I3- | XAI3-7 | XAI3-8
21 | IM1 | AI3 | 24VDC | Sink | 0-100 | % | TCV | AHU-A-TCV | AHU-A-TCV-FB | AHU A 3 WAY TCV POSITION FEEDBACK | - | - | - | - | I4+/I4- | XAI3-9 | XAI3-10
22 | IM1 | AI3 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I5+/I5- | XAI3-11 | XAI3-12
23 | IM1 | AI3 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I6+/I6- | XAI3-13 | XAI3-14
24 | IM1 | AI3 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I7+/I7- | XAI3-15 | XAI3-16
25 | IM2 | AI4 | 24VDC | Sink | 0-6 | pa | FIELD | 141-DPIT-0006 | DPIT-6 | DIFFERENTIAL PRESSURE TELECOM F&G ROOM | - | 1 | 5 | - | I0+/I0- | XAI4-1 | XAI4-2
26 | IM2 | AI4 | 24VDC | Sink | 0-6 | pa | FIELD | 141-DPIT-0007 | DPIT-7 | DIFFERENTIAL PRESSURE TELECOM F&G ROOM AIRLOCK | - | 1 | 5 | - | I1+/I1- | XAI4-3 | XAI4-4
27 | IM2 | AI4 | 24VDC | Sink | 0-6 | pa | FIELD | 141-DPIT-0008 | DPIT-8 | DIFFERENTIAL PRESSURE TEA ROOM | - | 1 | 5 | - | I2+/I2- | XAI4-5 | XAI4-6
28 | IM2 | AI4 | 24VDC | Sink | 0-6 | pa | FIELD | 141-DPIT-0009 | DPIT-9 | DIFFERENTIAL PRESSURE TOILET | - | 1 | 5 | - | I3+/I3- | XAI4-7 | XAI4-8
29 | IM2 | AI4 | 24VDC | Sink | 0-55 | °C | FIELD | 141-TT-0007 | TT-007 | E&I WORKSHOP TEMPERATURE | - | 20 | 30 | - | I4+/I4- | XAI4-9 | XAI4-10
30 | IM2 | AI4 | 24VDC | Sink | 0-55 | °C | FIELD | 141-TT-0008 | TT-008 | CONSUMABLE STORE TEMPERATURE | - | 20 | 30 | - | I5+/I5- | XAI4-11 | XAI4-12
31 | IM2 | AI4 | 24VDC | Sink | 0-55 | °C | FIELD | 141-TT-0009 | TT-009 | EU OPERATORS OFFICE TEMPERATURE | - | 20 | 30 | - | I6+/I6- | XAI4-13 | XAI4-14
32 | IM2 | AI4 | 24VDC | Sink | 0-55 | °C | FIELD | 141-TT-0010 | TT-010 | MAINTENANCE SUPERVISOR OFFICE TEMPERATURE | - | 20 | 30 | - | I7+/I7- | XAI4-15 | XAI4-16
33 | IM2 | AI5 | 24VDC | Sink | 0-55 | °C | FIELD | 141-TT-0011 | TT-011 | TEA ROOM TEMPERATURE | - | 20 | 30 | - | I0+/I0- | XAI5-1 | XAI5-2
34 | IM2 | AI5 | 24VDC | Sink | 0-55 | °C | FIELD | 141-TT-0012 | TT-012 | TOILET TEMPERATURE | - | 20 | 30 | - | I1+/I1- | XAI5-3 | XAI5-4
35 | IM2 | AI5 | 24VDC | Sink | 0-100 | RH | FIELD | 141-MT-0006 | MT-006 | CONSUMABLE STORE HUMIDITY | - | 30 | 60 | - | I2+/I2- | XAI5-5 | XAI5-6
36 | IM2 | AI5 | 24VDC | Sink | 0-100 | RH | FIELD | 141-MT-0007 | MT-007 | EU OPERATORS OFFICE HUMIDITY | - | 30 | 60 | - | I3+/I3- | XAI5-7 | XAI5-8
37 | IM2 | AI5 | 24VDC | Sink | 0-100 | RH | FIELD | 141-MT-0008 | MT-008 | MAINTENANCE SUPERVISOR OFFICE HUMIDITY | - | 30 | 60 | - | I4+/I4- | XAI5-9 | XAI5-10
38 | IM2 | AI5 | 24VDC | Sink | 0-100 | RH | FIELD | 141-MT-0009 | MT-009 | TEA ROOM HUMIDITY | - | 30 | 60 | - | I5+/I5- | XAI5-11 | XAI5-12
39 | IM2 | AI5 | 24VDC | Sink | 0-100 | RH | FIELD | 141-MT-0010 | MT-010 | TOILET HUMIDITY | - | 30 | 60 | - | I6+/I6- | XAI5-13 | XAI5-14
40 | IM2 | AI5 | 24VDC | Sink | 0-1560 | rpm | 141-ES-001B | 141-PC-0103B | CHLR2-PMP-SPD-FB | CHILLER-2 WATER PUMP SPEED FEEDBACK | - | - | - | - | I7+/I7- | XAI5-15 | XAI5-16
41 | IM2 | AI6 | 24VDC | Sink | 0-50 | HZ | 141-ES-001B | 141-GA-0101B | AHU2-FAN1-SPD-FB | AHU-2 FAN-1 SPEED FEEDBACK | - | - | - | - | I0+/I0- | XAI6-1 | XAI6-2
42 | IM2 | AI6 | 24VDC | Sink | 0-50 | HZ | 141-ES-001B | 141-GA-0101B | AHU2-FAN2-SPD-FB | AHU-2 FAN-2 SPEED FEEDBACK | - | - | - | - | I1+/I1- | XAI6-3 | XAI6-4
43 | IM2 | AI6 | 24VDC | Sink | 0-100 | % | TCV | AHU-B-TCV | AHU-B-TCV-FB | AHU B 3 WAY TCV POSITION FEEDBACK | - | - | - | - | I2+/I2- | XAI6-5 | XAI6-6
44 | IM2 | AI6 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I3+/I3- | XAI6-7 | XAI6-8
45 | IM2 | AI6 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I4+/I4- | XAI6-9 | XAI6-10
46 | IM2 | AI6 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I5+/I5- | XAI6-11 | XAI6-12
47 | IM2 | AI6 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I6+/I6- | XAI6-13 | XAI6-14
48 | IM2 | AI6 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I7+/I7- | XAI6-15 | XAI6-16

## AO
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
OPERATING SHELTER
RUWAIS - U.A.E.
[10 empty] | FACILITY NAME: BOROUGE 4 | [5 empty] | COMPANY PROJ. NO. |  | 4700000897
[16 empty] | CONTRACTOR. PROJ. NO. |  | 083118C
| OS-HVAC-CP | [8 empty] | DOCUMENT TITLE: OS HVAC PLC System - I/O List REV 4 | [5 empty] | SUBCONTR. ID |  | -
Sl. No. | IM Module | I/O Detail |  |  |  |  | TO | EQUIPMENT TAG | PLC TAG | Description | Alarm Setpoints |  |  |  | PLC Term. | TB GROUP |  | Verified & Signed
|  | Module | Supply | Type | Range | Unit |  |  |  |  | LL | L | H | HH
ANALOGUE OUTPUT
1 | IM1 | AO1 | 24VDC | 4-20mA | - | - | AHU-1 | 141-GA-0101A | AHU1-FAN1-SPD-REF | AHU-1 FAN-1 SPEED SETPOINT | - | - | - | - | Q0+/Q0- | XAO1-1 | XAO1-2
2 | IM1 | AO1 | 24VDC | 4-20mA | - | - | AHU-1 | 141-GA-0101A | AHU1-FAN2-SPD-REF | AHU-1 FAN-2 SPEED SETPOINT | - | - | - | - | Q1+/Q1- | XAO1-3 | XAO1-4
3 | IM1 | AO1 | 24VDC | 4-20mA | - | - | CWP | 141-PC-0103A | CHLR1-PMP-SPD-REF | CHILLER-1 WATER PUMP SPEED SETPOINT | - | - | - | - | Q2+/Q2- | XAO1-5 | XAO1-6
4 | IM1 | AO1 | 24VDC | 4-20mA | - | - | - | 141-GD-0335 | 141-GD-0335-SP | MODULATING FRESH AIR DAMPER MD-0335 SETPOINT | - | - | - | - | Q3+/Q3- | XAO1-7 | XAO1-8
5 | IM1 | AO2 | 24VDC | 4-20mA | - | - | TCV | AHU-A-TCV | AHU-A-TCV-SP | AHU A 3 WAY TCV SETPOINT | - | - | - | - | Q0+/Q0- | XAO2-1 | XAO2-2
6 | IM1 | AO2 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q1+/Q1- | XAO2-3 | XAO2-4
7 | IM1 | AO2 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q2+/Q2- | XAO2-5 | XAO2-6
8 | IM1 | AO2 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q3+/Q3- | XAO2-7 | XAO2-8
9 | IM2 | AO3 | 24VDC | 4-20mA | - | - | AHU-2 | 141-GA-0101B | AHU2-FAN1-SPD-REF | AHU-2 FAN-1 SPEED SETPOINT | - | - | - | - | Q0+/Q0- | XAO3-1 | XAO3-2
10 | IM2 | AO3 | 24VDC | 4-20mA | - | - | AHU-2 | 141-GA-0101B | AHU2-FAN2-SPD-REF | AHU-2 FAN-2 SPEED SETPOINT | - | - | - | - | Q1+/Q1- | XAO3-3 | XAO3-4
11 | IM2 | AO3 | 24VDC | 4-20mA | - | - | CWP | 141-PC-0103B | CHLR2-PMP-SPD-REF | CHILLER-2 WATER PUMP SPEED SETPOINT | - | - | - | - | Q2+/Q2- | XAO3-5 | XAO3-6
12 | IM2 | AO3 | 24VDC | 4-20mA | - | - | TCV | AHU-B-TCV | AHU-B-TCV-SP | AHU B 3 WAY TCV SETPOINT | - | - | - | - | Q3+/Q3- | XAO3-7 | XAO3-8
13 | IM2 | AO4 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q0+/Q0- | XAO4-1 | XAO4-2
14 | IM2 | AO4 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q1+/Q1- | XAO4-3 | XAO4-4
15 | IM2 | AO4 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q2+/Q2- | XAO4-5 | XAO4-6
16 | IM2 | AO4 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q3+/Q3- | XAO4-7 | XAO4-8

## IO Summary
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
OPERATING SHELTER
RUWAIS - U.A.E.
[8 empty] | FACILITY NAME: BOROUGE 4 | COMPANY PROJ. NO. | 4700000897
[9 empty] | CONTRACTOR. PROJ. NO. | 083118C
OS-HVAC-CP | [7 empty] | DOCUMENT TITLE: OS HVAC PLC System - I/O List REV 4 | SUBCONTR. ID | -
IO SUMMARY
Sl.No | Type | No. Of Channels | No. Of Modules | Count | Used | Spare | Spare %
1 | DI | 16 | 11 | 176 | 147 | 29 | 19.7279
3 | DO | 16 | 4 | 64 | 57 | 7 | 12.2807
4 | AI | 8 | 6 | 48 | 40 | 8 | 20
5 | AO | 4 | 4 | 16 | 9 | 7 | 77.7778

## MODBUS_LIST
OPERATING SHELTER HVAC DCS INTERFACE SIGNALS
S.NO | EQUIPMENT TAG | TAG NAME | DESSCRIPTION | MULTIPLICATION FACTOR | DATA TYPE | SIGNAL FROM | SIGNAL TO | STATE 0 | STATE 1 | MODBUS ADDRESS | BIT | REMARKS
1 | 141-GC-0103A | CHLR1_RUN | CHILLER-1 UNIT RUN STATUS |  | BOOL | PLC | DCS | STOPPED | RUNNING | 40001 | 0
2 | 141-GC-0103A | CHLR1_TRP | CHILLER-1 UNIT TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40001 | 1
3 | 141-GC-0103A | CHLR1_RMT | CHILLER-1 REMOTE MODE STATUS |  | BOOL | PLC | DCS | LOCAL | REMOTE | 40001 | 2
4 | 141-GC-0103A | CHLR1_BRK_TRP | CHILLER-1 UNIT BREAKER TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40001 | 3
5 | 141-GC-0103A | CHLR1_FS | CHILLER-1 FLOW SWITCH STATUS |  | BOOL | PLC | DCS | NO FLOW | FLOW ON | 40001 | 4
6 | 141-GA-0101A | AHU1_RUN | AHU-1 RUN STATUS |  | BOOL | PLC | DCS | STOPPED | RUNNING | 40001 | 5
7 | - | - | SPARE |  | BOOL | PLC | DCS |  |  | 40001 | 6
8 | 141-GA-0101A | AHU1_RMT | AHU-1 REMOTE MODE STATUS |  | BOOL | PLC | DCS | LOCAL | REMOTE | 40001 | 7
9 | 141-GA-0101A | AHU1_BRK_TRP | AHU-1 UNIT BREAKER TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40001 | 8
10 | 141-GA-0101A | AHU1_PF_DPS | AHU-1 PRE-FILTER DIFFERENTIAL PRESSURE HIGH |  | BOOL | PLC | DCS | NORMAL | ALARM | 40001 | 9
11 | 141-GA-0101A | AHU1_FF_DPS | AHU-1 FINE-FILTER DIFFERENTIAL PRESSURE HIGH |  | BOOL | PLC | DCS | NORMAL | ALARM | 40001 | 10
12 | 141-GA-0101A | AHU1_AF_DPS | AHU-1 FAN AIR FLOW DIFFERENTIAL PRESSURE |  | BOOL | PLC | DCS | NO FLOW | FLOW ON | 40001 | 11
13 | 141-GK-0101A | TLT_FAN1_RUN | TOILET ROOM FAN-1 RUN STATUS |  | BOOL | PLC | DCS | STOPPED | RUNNING | 40001 | 12
14 | 141-GK-0101A | TLT_FAN1_TRP | TOILET ROOM FAN-1 TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40001 | 13
15 | 141-GK-0101A | TLT_FAN1_RMT | TOILET ROOM FAN-1 REMOTE MODE STATUS |  | BOOL | PLC | DCS | LOCAL | REMOTE | 40001 | 14
16 | 141-GK-0101A | TLT_FAN1_ES | TOILET ROOM FAN-1 EMERGENCY STOP |  | BOOL | PLC | DCS | NORMAL | ACTIVE | 40001 | 15
17 | 141-GK-0101A | TLT_FAN1&2_DPS | DIFFERENTIAL PRESSURE ACROSS TOILET ROOM FAN-1&2 |  | BOOL | PLC | DCS | NO FLOW | FLOW ON | 40002 | 0
18 | 141-PC-0103A | CHLR1_PMP_RUN | CHILLER-1 WATER PUMP RUN STATUS |  | BOOL | PLC | DCS | STOPPED | RUNNING | 40002 | 1
19 | 141-PC-0103A | CHLR1_PMP_TRP | CHILLER-1 WATER PUMP TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40002 | 2
20 | 141-PC-0103A | CHLR1_PMP_RMT | CHILLER-1 WATER PUMP REMOTE MODE STATUS |  | BOOL | PLC | DCS | LOCAL | REMOTE | 40002 | 3
21 | 141-PC-0103A | CHLR1_PMP_ES | CHILLER-1 WATER PUMP EMERGENCY STOP |  | BOOL | PLC | DCS | NORMAL | ACTIVE | 40002 | 4
22 | - | BLD_FAN_RUN | BLEED FAN RUN STATUS |  | BOOL | PLC | DCS | STOPPED | RUNNING | 40002 | 5
23 | - | BLD_FAN_TRP | BLEED FAN TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40002 | 6
24 | - | BLD_FAN_RMT | BLEED FAN REMOTE MODE STATUS |  | BOOL | PLC | DCS | LOCAL | REMOTE | 40002 | 7
25 | - | BLD_FAN_ES | BLEED FAN EMERGENCY STOP |  | BOOL | PLC | DCS | NORMAL | ACTIVE | 40002 | 8
26 | - | AHU1-BFV-ZIO | MOTORIZED BUTTER FLY VALVE AHU-1 OPEN STATUS |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40002 | 9
27 | - | AHU1-BFV-ZIC | MOTORIZED BUTTER FLY VALVE AHU-1 CLOSE STATUS |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40002 | 10
28 | 141-GD-0331 | 141-GD-0331-ZIO | MOTORIZED SHUTOFF DAMPER 141-GD-0331 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40002 | 11
29 | 141-GD-0331 | 141-GD-0331-ZIC | MOTORIZED SHUTOFF DAMPER 141-GD-0331 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40002 | 12
30 | 141-GD-0332 | 141-GD-0332-ZIO | MOTORIZED SHUTOFF DAMPER 141-GD-0332 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40002 | 13
31 | 141-GD-0332 | 141-GD-0332-ZIC | MOTORIZED SHUTOFF DAMPER 141-GD-0332 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40002 | 14
32 | 141-GD-0336 | 141-GD-0336-ZIO | MOTORIZED SHUTOFF DAMPER 141-GD-0336 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40002 | 15
33 | 141-GD-0336 | 141-GD-0336-ZIC | MOTORIZED SHUTOFF DAMPER 141-GD-0336 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40003 | 0
34 | 141-GD-0301 | 141-GD-0301-ZIO | MOTORIZED GAS DAMPER 141-GD-0301 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40003 | 1
35 | 141-GD-0301 | 141-GD-0301-ZIC | MOTORIZED GAS DAMPER 141-GD-0301 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40003 | 2
36 | 141-GD-0302 | 141-GD-0302-ZIO | MOTORIZED GAS DAMPER 141-GD-0302 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40003 | 3
37 | 141-GD-0302 | 141-GD-0302-ZIC | MOTORIZED GAS DAMPER 141-GD-0302 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40003 | 4
38 | 141-GD-0303 | 141-GD-0303-ZIO | MOTORIZED GAS DAMPER 141-GD-0303 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40003 | 5
39 | 141-GD-0303 | 141-GD-0303-ZIC | MOTORIZED GAS DAMPER 141-GD-0303 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40003 | 6
40 | 141-GD-0304 | 141-GD-0304-ZIO | MOTORIZED GAS DAMPER 141-GD-0304 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40003 | 7
41 | 141-GD-0304 | 141-GD-0304-ZIC | MOTORIZED GAS DAMPER 141-GD-0304 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40003 | 8
42 | 141-GD-0305 | 141-GD-0305-ZIO | MOTORIZED GAS DAMPER 141-GD-0305 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40003 | 9
43 | 141-GD-0305 | 141-GD-0305-ZIC | MOTORIZED GAS DAMPER 141-GD-0305 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40003 | 10
44 | 141-GD-0306 | 141-GD-0306-ZIO | MOTORIZED GAS DAMPER 141-GD-0306 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40003 | 11
45 | 141-GD-0306 | 141-GD-0306-ZIC | MOTORIZED GAS DAMPER 141-GD-0306 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40003 | 12
46 | 141-GD-0307 | 141-GD-0307-ZIO | MOTORIZED GAS DAMPER 141-GD-0307 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40003 | 13
47 | 141-GD-0307 | 141-GD-0307-ZIC | MOTORIZED GAS DAMPER 141-GD-0307 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40003 | 14
48 | 141-GD-0308 | 141-GD-0308-ZIO | MOTORIZED GAS DAMPER 141-GD-0308 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40003 | 15
49 | 141-GD-0308 | 141-GD-0308-ZIC | MOTORIZED GAS DAMPER 141-GD-0308 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40004 | 0
50 | 141-GD-0309 | 141-GD-0309-ZIO | MOTORIZED GAS DAMPER 141-GD-0309 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40004 | 1
51 | 141-GD-0309 | 141-GD-0309-ZIC | MOTORIZED GAS DAMPER 141-GD-0309 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40004 | 2
52 | 141-GD-0310 | 141-GD-0310-ZIO | MOTORIZED GAS DAMPER 141-GD-0310 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40004 | 3
53 | 141-GD-0310 | 141-GD-0310-ZIC | MOTORIZED GAS DAMPER 141-GD-0310 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40004 | 4
54 | 141-GD-0311 | 141-GD-0311-ZIO | MOTORIZED GAS DAMPER 141-GD-0311 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40004 | 5
55 | 141-GD-0311 | 141-GD-0311-ZIC | MOTORIZED GAS DAMPER 141-GD-0311 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40004 | 6
56 | 141-GD-0312 | 141-GD-0312-ZIO | MOTORIZED GAS DAMPER 141-GD-0312 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40004 | 7
57 | 141-GD-0312 | 141-GD-0312-ZIC | MOTORIZED GAS DAMPER 141-GD-0312 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40004 | 8
58 | 141-GD-0313 | 141-GD-0313-ZIO | MOTORIZED GAS DAMPER 141-GD-0313 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40004 | 9
59 | 141-GD-0313 | 141-GD-0313-ZIC | MOTORIZED GAS DAMPER 141-GD-0313 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40004 | 10
60 | 141-GD-0314 | 141-GD-0314-ZIO | MOTORIZED GAS DAMPER 141-GD-0314 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40004 | 11
61 | 141-GD-0314 | 141-GD-0314-ZIC | MOTORIZED GAS DAMPER 141-GD-0314 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40004 | 12
62 | 141-GB-0119 | MW_HTR_TRP | MACHINE WORKSHOP HEATER TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40004 | 13
63 | 141-GB-0119 | MW_HTR_ON | MACHINE WORKSHOP HEATER ON/OFF STATUS |  | BOOL | PLC | DCS | OFF | ON | 40004 | 14
64 | 141-GB-0105 | EIW_HTR_TRP | E&I WORKSHOP HEATER TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40004 | 15
65 | 141-GB-0105 | EIW_HTR_ON | E&I WORKSHOP HEATER ON/OFF STATUS |  | BOOL | PLC | DCS | OFF | ON | 40005 | 0
66 | 141-GB-0104 | MTO_HTR_TRP | MAINTENANCE TECHNICIAN OFFICE HEATER TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40005 | 1
67 | 141-GB-0104 | MTO_HTR_ON | MAINTENANCE TECHNICIAN OFFICE HEATER ON/OFF STATUS |  | BOOL | PLC | DCS | OFF | ON | 40005 | 2
68 | 141-GB-0103 | TLR_HTR_TRP | TELECOM ROOM HEATER TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40005 | 3
69 | 141-GB-0103 | TLR_HTR_ON | TELECOM ROOM HEATER ON/OFF STATUS |  | BOOL | PLC | DCS | OFF | ON | 40005 | 4
70 | - | EMG_STP | HVACP EMERGENCY STOP |  | BOOL | PLC | DCS | NORMAL | ACTIVE | 40005 | 5
71 | - | MUTE_PB | MUTE PUSH BUTTON |  | BOOL | PLC | DCS | OFF | ON | 40005 | 6
72 | - | RST_PB | RESET PUSH BUTTON |  | BOOL | PLC | DCS | OFF | ON | 40005 | 7
73 | - | PSU1&2_HLTHY | POWER SUPPLY 1 & 2 HEALTHY |  | BOOL | PLC | DCS | UNHEALTHY | HEALTHY | 40005 | 8
74 | - | AFS_HLTHY | PANEL AIR FLOW SWITCH HEALTHY |  | BOOL | PLC | DCS | UNHEALTHY | HEALTHY | 40005 | 9
75 | - | INC1_ON | MAIN INCOMER-1 ON/OFF STATUS |  | BOOL | PLC | DCS | OPEN | CLOSE | 40005 | 10
76 | - | INC1_TRP | MAIN INCOMER-1 TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40005 | 11
77 | - | INC2_ON | MAIN INCOMER-2 ON/OFF STATUS |  | BOOL | PLC | DCS | OPEN | CLOSE | 40005 | 12
78 | - | INC2_TRP | MAIN INCOMER-2 TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40005 | 13
79 | 141-GA-0101A | AHU1_FAN2_RUN | AHU-1 FAN-2 RUN STATUS |  | BOOL | PLC | DCS | STOPPED | RUNNING | 40005 | 14
80 | 141-GA-0101A | AHU1_FAN2_RMT | AHU-1 FAN-2 REMOTE MODE STATUS |  | BOOL | PLC | DCS | LOCAL | REMOTE | 40005 | 15
81 | 141-GA-0101A | AHU1_FAN2_BRK_TRP | AHU-1 FAN-2 BREAKER TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40006 | 0
82 | - | CHLR1-BFV-ZIO | MOTORIZED BUTTER FLY VALVE CHILLER-1 OPEN STATUS |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40006 | 1
83 | - | CHLR1-BFV-ZIC | MOTORIZED BUTTER FLY VALVE CHILLER-1 CLOSE STATUS |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40006 | 2
84 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40006 | 3
85 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40006 | 4
86 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40006 | 5
87 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40006 | 6
88 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40006 | 7
89 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40006 | 8
90 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40006 | 9
91 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40006 | 10
92 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40006 | 11
93 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40006 | 12
94 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40006 | 13
95 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40006 | 14
96 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40006 | 15
97 | 141-GC-0103B | CHLR2_RUN | CHILLER-2 UNIT RUN STATUS |  | BOOL | PLC | DCS | STOPPED | RUNNING | 40007 | 0
98 | 141-GC-0103B | CHLR2_TRP | CHILLER-2 UNIT TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40007 | 1
99 | 141-GC-0103B | CHLR2_RMT | CHILLER-2 REMOTE MODE STATUS |  | BOOL | PLC | DCS | LOCAL | REMOTE | 40007 | 2
100 | 141-GC-0103B | CHLR2_BRK_TRP | CHILLER-2 UNIT BREAKER TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40007 | 3
101 | 141-GC-0103B | CHLR2_FS | CHILLER-2 FLOW SWITCH STATUS |  | BOOL | PLC | DCS | NO FLOW | FLOW ON | 40007 | 4
102 | 141-GA-0101B | AHU2_RUN | AHU-2 RUN STATUS |  | BOOL | PLC | DCS | STOPPED | RUNNING | 40007 | 5
103 | - | - | SPARE |  | BOOL | PLC | DCS |  |  | 40007 | 6
104 | 141-GA-0101B | AHU2_RMT | AHU-2 REMOTE MODE STATUS |  | BOOL | PLC | DCS | LOCAL | REMOTE | 40007 | 7
105 | 141-GA-0101B | AHU2_BRK_TRP | AHU-2 UNIT BREAKER TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40007 | 8
106 | 141-GA-0101B | AHU2_PF_DPS | AHU-2 PRE-FILTER DIFFERENTIAL PRESSURE HIGH |  | BOOL | PLC | DCS | NORMAL | ALARM | 40007 | 9
107 | 141-GA-0101B | AHU2_FF_DPS | AHU-2 FINE-FILTER DIFFERENTIAL PRESSURE HIGH |  | BOOL | PLC | DCS | NORMAL | ALARM | 40007 | 10
108 | 141-GA-0101B | AHU2_AF_DPS | AHU-2 FAN AIR FLOW DIFFERENTIAL PRESSURE |  | BOOL | PLC | DCS | NO FLOW | FLOW ON | 40007 | 11
109 | 141-GK-0101B | TLT_FAN2_RUN | TOILET ROOM FAN-2 RUN STATUS |  | BOOL | PLC | DCS | STOPPED | RUNNING | 40007 | 12
110 | 141-GK-0101B | TLT_FAN2_TRP | TOILET ROOM FAN-2 TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40007 | 13
111 | 141-GK-0101B | TLT_FAN2_RMT | TOILET ROOM FAN-2 REMOTE MODE STATUS |  | BOOL | PLC | DCS | LOCAL | REMOTE | 40007 | 14
112 | 141-GK-0101B | TLT_FAN2_ES | TOILET ROOM FAN-2 EMERGENCY STOP |  | BOOL | PLC | DCS | NORMAL | ACTIVE | 40007 | 15
113 | 141-PC-0103B | CHLR2_PMP_RUN | CHILLER-2 WATER PUMP RUN STATUS |  | BOOL | PLC | DCS | STOPPED | RUNNING | 40008 | 0
114 | 141-PC-0103B | CHLR2_PMP_TRP | CHILLER-2 WATER PUMP TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40008 | 1
115 | 141-PC-0103B | CHLR2_PMP_RMT | CHILLER-2 WATER PUMP REMOTE MODE STATUS |  | BOOL | PLC | DCS | LOCAL | REMOTE | 40008 | 2
116 | 141-PC-0103B | CHLR2_PMP_ES | CHILLER-2 WATER PUMP EMERGENCY STOP |  | BOOL | PLC | DCS | NORMAL | ACTIVE | 40008 | 3
117 | - | AHU2-BFV-ZIO | MOTORIZED BUTTER FLY VALVE AHU-2 OPEN STATUS |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40008 | 4
118 | - | AHU2-BFV-ZIC | MOTORIZED BUTTER FLY VALVE AHU-2 CLOSE STATUS |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40008 | 5
119 | 141-GD-0333 | 141-GD-0333-ZIO | MOTORIZED SHUTOFF DAMPER 141-GD-0333 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40008 | 6
120 | 141-GD-0333 | 141-GD-0333-ZIC | MOTORIZED SHUTOFF DAMPER 141-GD-0333 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40008 | 7
121 | 141-GD-0334 | 141-GD-0334-ZIO | MOTORIZED SHUTOFF DAMPER 141-GD-0334 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40008 | 8
122 | 141-GD-0334 | 141-GD-0334-ZIC | MOTORIZED SHUTOFF DAMPER 141-GD-0334 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40008 | 9
123 | 141-GD-0315 | 141-GD-0315-ZIO | MOTORIZED GAS DAMPER 141-GD-0315 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40008 | 10
124 | 141-GD-0315 | 141-GD-0315-ZIC | MOTORIZED GAS DAMPER 141-GD-0315 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40008 | 11
125 | 141-GD-0316 | 141-GD-0316-ZIO | MOTORIZED GAS DAMPER 141-GD-0316 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40008 | 12
126 | 141-GD-0316 | 141-GD-0316-ZIC | MOTORIZED GAS DAMPER 141-GD-0316 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40008 | 13
127 | 141-GD-0317 | 141-GD-0317-ZIO | MOTORIZED GAS DAMPER 141-GD-0317 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40008 | 14
128 | 141-GD-0317 | 141-GD-0317-ZIC | MOTORIZED GAS DAMPER 141-GD-0317 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40008 | 15
129 | 141-GD-0318 | 141-GD-0318-ZIO | MOTORIZED GAS DAMPER 141-GD-0318 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40009 | 0
130 | 141-GD-0318 | 141-GD-0318-ZIC | MOTORIZED GAS DAMPER 141-GD-0318 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40009 | 1
131 | 141-GD-0319 | 141-GD-0319-ZIO | MOTORIZED GAS DAMPER 141-GD-0319 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40009 | 2
132 | 141-GD-0319 | 141-GD-0319-ZIC | MOTORIZED GAS DAMPER 141-GD-0319 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40009 | 3
133 | 141-GD-0320 | 141-GD-0320-ZIO | MOTORIZED GAS DAMPER 141-GD-0320 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40009 | 4
134 | 141-GD-0320 | 141-GD-0320-ZIC | MOTORIZED GAS DAMPER 141-GD-0320 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40009 | 5
135 | 141-GD-0321 | 141-GD-0321-ZIO | MOTORIZED GAS DAMPER 141-GD-0321 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40009 | 6
136 | 141-GD-0321 | 141-GD-0321-ZIC | MOTORIZED GAS DAMPER 141-GD-0321 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40009 | 7
137 | 141-GD-0322 | 141-GD-0322-ZIO | MOTORIZED GAS DAMPER 141-GD-0322 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40009 | 8
138 | 141-GD-0322 | 141-GD-0322-ZIC | MOTORIZED GAS DAMPER 141-GD-0322 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40009 | 9
139 | 141-GD-0323 | 141-GD-0323-ZIO | MOTORIZED GAS DAMPER 141-GD-0323 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40009 | 10
140 | 141-GD-0323 | 141-GD-0323-ZIC | MOTORIZED GAS DAMPER 141-GD-0323 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40009 | 11
141 | 141-GD-0324 | 141-GD-0324-ZIO | MOTORIZED GAS DAMPER 141-GD-0324 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40009 | 12
142 | 141-GD-0324 | 141-GD-0324-ZIC | MOTORIZED GAS DAMPER 141-GD-0324 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40009 | 13
143 | 141-GD-0325 | 141-GD-0325-ZIO | MOTORIZED GAS DAMPER 141-GD-0325 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40009 | 14
144 | 141-GD-0325 | 141-GD-0325-ZIC | MOTORIZED GAS DAMPER 141-GD-0325 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40009 | 15
145 | 141-GD-0326 | 141-GD-0326-ZIO | MOTORIZED GAS DAMPER 141-GD-0326 OPEN FEEDBACK |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40010 | 0
146 | 141-GD-0326 | 141-GD-0326-ZIC | MOTORIZED GAS DAMPER 141-GD-0326 CLOSE FEEDBACK |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40010 | 1
147 | - | MSU_HTR_TRP | MAINTENANCE SUPERVISOR OFFICE HEATER TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40010 | 2
148 | - | MSU_HTR_ON | MAINTENANCE SUPERVISOR OFFICE HEATER ON/OFF STATUS |  | BOOL | PLC | DCS | OFF | ON | 40010 | 3
149 | - | EUO_HTR_TRP | EU OPERATORS OFFICE HEATER TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40010 | 4
150 | - | EUO_HTR_ON | EU OPERATORS OFFICE HEATER ON/OFF STATUS |  | BOOL | PLC | DCS | OFF | ON | 40010 | 5
151 | - | TR_HTR_TRP | TEA ROOM HEATER TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40010 | 6
152 | - | TR_HTR_ON | TEA ROOM HEATER ON/OFF STATUS |  | BOOL | PLC | DCS | OFF | ON | 40010 | 7
153 | - | HVAC_SHUT | HVAC SHUTDOWN COMMAND FROM F&G AND ALL DAMPERS CLOSE |  | BOOL | PLC | DCS | NORMAL | SHUTDOWN | 40010 | 8
154 | - | HVAC_RECR | HVAC RECIRCULATION MODE FROM F&G AND AIR INTAKE DAMPER CLOSE |  | BOOL | PLC | DCS | NORMAL | RECIRCUL | 40010 | 9
155 | - | HVAC_H2_HIGH | HVAC HYDROGEN HIGH IN TOILET ROOM FROM F&G |  | BOOL | PLC | DCS | NORMAL | H2 HIGH | 40010 | 10
156 | 141-GB-0120 | HVAC_RM_HTR_TRP | HVAC ROOM HEATER TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40010 | 11
157 | 141-GB-0120 | HVAC_RM_HTR_ON | HVAC ROOM HEATER ON/OFF STATUS |  | BOOL | PLC | DCS | OFF | ON | 40010 | 12
158 | 141-GA-0101B | AHU2_FAN2_RUN | AHU-2 FAN-2 RUN STATUS |  | BOOL | PLC | DCS | STOPPED | RUNNING | 40010 | 13
159 | 141-GA-0101B | AHU2_FAN2_RMT | AHU-2 FAN-2 REMOTE MODE STATUS |  | BOOL | PLC | DCS | LOCAL | REMOTE | 40010 | 14
160 | 141-GA-0101B | AHU2_FAN2_BRK_TRP | AHU-2 FAN-2 BREAKER TRIP STATUS |  | BOOL | PLC | DCS | NORMAL | TRIP | 40010 | 15
161 | - | CHLR2-BFV-ZIO | MOTORIZED BUTTER FLY VALVE CHILLER-2 OPEN STATUS |  | BOOL | PLC | DCS | NOT OPEN | OPEN | 40011 | 0
162 | - | CHLR2-BFV-ZIC | MOTORIZED BUTTER FLY VALVE CHILLER-2 CLOSE STATUS |  | BOOL | PLC | DCS | NOT CLOSE | CLOSE | 40011 | 1
163 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40011 | 2
164 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40011 | 3
165 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40011 | 4
166 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40011 | 5
167 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40011 | 6
168 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40011 | 7
169 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40011 | 8
170 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40011 | 9
171 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40011 | 10
172 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40011 | 11
173 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40011 | 12
174 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40011 | 13
175 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40011 | 14
176 | - | - | SPARE |  | BOOL | PLC | DCS | - | - | 40011 | 15
S.NO | EQUIPMENT TAG | TAG NAME | DESSCRIPTION | MULTIPLICATION FACTOR | DATA TYPE | SIGNAL FROM | SIGNAL TO | RANGE | HIGH SET POINT | MODBUS ADDRESS | BIT
177 | 141-DPIT-0001 | DPIT-1 | DIFFERENTIAL PRESSURE FRESH AIR DUCT | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-6 pa | - | 40020 | -
178 | 141-DPIT-0002 | DPIT-2 | DIFFERENTIAL PRESSURE HVAC ROOM | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-6 pa | - | 40021 | -
179 | 141-DPIT-0003 | DPIT-3 | DIFFERENTIAL PRESSURE EQUIPMENT TOOL ROOM | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-6 pa | - | 40022 | -
180 | 141-DPIT-0004 | DPIT-4 | DIFFERENTIAL PRESSURE E&I WORKSHOP AIRLOCK | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-6 pa | - | 40023 | -
181 | 141-DPIT-0005 | DPIT-5 | DIFFERENTIAL PRESSURE MAINTENANCE SUPERVISOR OFFICE | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-6 pa | - | 40024 | -
182 | 141-TT-0001 | TT-001 | FRESH AIR DUCT TEMPERATURE | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-55 °C | - | 40025 | -
183 | 141-TT-0002 | TT-002 | COMMON SUPPLY AIR DUCT TEMPERATURE | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-55 °C | - | 40026 | -
184 | 141-TT-0003 | TT-003 | COMMON RETURN AIR DUCT TEMPERATURE | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-55 °C | - | 40027 | -
185 | 141-TT-0004 | TT-004 | HVAC ROOM TEMPERATURE | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-55 °C | - | 40028 | -
186 | 141-TT-0005 | TT-005 | EQUIPMENT TOOL ROOM TEMPERATURE | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-55 °C | - | 40029 | -
187 | 141-TT-0006 | TT-006 | MACHINE WORKSHOP TEMPERATURE | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-55 °C | - | 40030 | -
188 | 141-MT-0001 | MT-001 | COMMON RETURN AIR DUCT HUMIDITY | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-100 RH | - | 40031 | -
189 | 141-MT-0002 | MT-002 | HVAC ROOM HUMIDITY | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-100 RH | - | 40032 | -
190 | 141-MT-0003 | MT-003 | EQUIPMENT TOOL ROOM HUMIDITY | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-100 RH | - | 40033 | -
191 | 141-MT-0004 |  | MACHANICAL WORKSHOP HUMIDITY | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-100 RH | - | 40034 | -
192 | 141-MT-0005 | MT-005 | E&I WORKSHOP HUMIDITY | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-100 RH | - | 40035 | -
193 | 141-PC-0103A | CHLR1-PMP-SPD-FB | CHILLER-1 WATER PUMP SPEED FEEDBACK | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-50 HZ | - | 40036 | -
194 | 141-GD-0335 | 141-GD-0335-FB | MODULATING FRESH AIR DAMPER MD-0335 POSITION FEEDBACK | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-100 % | - | 40037 | -
195 | 141-GA-0101A | AHU1-FAN1-SPD-FB | AHU-1 FAN-1 SPEED FEEDBACK | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-50 HZ | - | 40038 | -
196 | 141-GA-0101A | AHU1-FAN2-SPD-FB | AHU-1 FAN-2 SPEED FEEDBACK | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-50 HZ | - | 40039 | -
197 | AHU-A-TCV | AHU-A-TCV-FB | AHU A 3 WAY TCV POSITION FEEDBACK | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-100 % | - | 40040 | -
198 | - | - | SPARE | DIVIDED BY 100 | INTEGER | PLC | DCS | - | - | 40041 | -
199 | - | - | SPARE | DIVIDED BY 100 | INTEGER | PLC | DCS | - | - | 40042 | -
200 | - | - | SPARE | DIVIDED BY 100 | INTEGER | PLC | DCS | - | - | 40043 | -
201 | 141-DPIT-0006 | DPIT-6 | DIFFERENTIAL PRESSURE TELECOM F&G ROOM | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-6 pa | - | 40044 | -
202 | 141-DPIT-0007 | DPIT-7 | DIFFERENTIAL PRESSURE TELECOM F&G ROOM AIRLOCK | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-6 pa | - | 40045 | -
203 | 141-DPIT-0008 | DPIT-8 | DIFFERENTIAL PRESSURE TEA ROOM | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-6 pa | - | 40046 | -
204 | 141-DPIT-0009 | DPIT-9 | DIFFERENTIAL PRESSURE TOILET | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-6 pa | - | 40047 | -
205 | 141-TT-0007 | TT-007 | E&I WORKSHOP TEMPERATURE | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-55 °C | - | 40048 | -
206 | 141-TT-0008 | TT-008 | CONSUMABLE STORE TEMPERATURE | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-55 °C | - | 40049 | -
207 | 141-TT-0009 | TT-009 | EU OPERATORS OFFICE TEMPERATURE | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-55 °C | - | 40050 | -
208 | 141-TT-0010 | TT-010 | MAINTENANCE SUPERVISOR OFFICE TEMPERATURE | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-55 °C | - | 40051 | -
209 | 141-TT-0011 | TT-011 | TEA ROOM TEMPERATURE | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-55 °C | - | 40052 | -
210 | 141-TT-0012 | TT-012 | TOILET TEMPERATURE | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-55 °C | - | 40053 | -
211 | 141-MT-0006 | MT-006 | CONSUMABLE STORE HUMIDITY | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-100 RH | - | 40054 | -
212 | 141-MT-0007 | MT-007 | EU OPERATORS OFFICE HUMIDITY | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-100 RH | - | 40055 | -
213 | 141-MT-0008 | MT-008 | MAINTENANCE SUPERVISOR OFFICE HUMIDITY | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-100 RH | - | 40056 | -
214 | 141-MT-0009 | MT-009 | TEA ROOM HUMIDITY | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-100 RH | - | 40057 | -
215 | 141-MT-0010 | MT-010 | TOILET HUMIDITY | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-100 RH | - | 40058 | -
216 | 141-PC-0103B | CHLR2-PMP-SPD-FB | CHILLER-2 WATER PUMP SPEED FEEDBACK | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-50 HZ | - | 40059 | -
217 | 141-GA-0101B | AHU2-FAN1-SPD-FB | AHU-2 FAN-1 SPEED FEEDBACK | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-50 HZ | - | 40060 | -
218 | 141-GA-0101B | AHU2-FAN2-SPD-FB | AHU-2 FAN-2 SPEED FEEDBACK | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-50 HZ | - | 40061 | -
219 | AHU-B-TCV | AHU-B-TCV-FB | AHU B 3 WAY TCV POSITION FEEDBACK | DIVIDED BY 100 | INTEGER | PLC | DCS | 0-100 % | - | 40062 | -
220 | - | - | SPARE | DIVIDED BY 100 | INTEGER | PLC | DCS | - | - | 40063 | -
221 | - | - | SPARE | DIVIDED BY 100 | INTEGER | PLC | DCS | - | - | 40064 | -
222 | - | - | SPARE | DIVIDED BY 100 | INTEGER | PLC | DCS | - | - | 40065 | -
223 | - | - | SPARE | DIVIDED BY 100 | INTEGER | PLC | DCS | - | - | 40066 | -
224 | - | - | SPARE | DIVIDED BY 100 | INTEGER | PLC | DCS | - | - | 40067 | -

## INSTRUMENT_LIST
TRANSMITTERS |  | DPS/FS
DPIT-1 | DIFFERENTIAL PRESSURE FRESH AIR DUCT | CHLR1_FS | CHILLER-1 FLOW SWITCH STATUS
DPIT-2 | DIFFERENTIAL PRESSURE HVAC ROOM | CHLR2_FS | CHILLER-1 FLOW SWITCH STATUS
DPIT-3 | DIFFERENTIAL PRESSURE EQUIPMENT TOOL ROOM | AHU1_PF_DPS | AHU-1 PRE-FILTER DIFFERENTIAL PRESSURE HIGH
DPIT-4 | DIFFERENTIAL PRESSURE E&I WORKSHOP AIRLOCK | AHU1_FF_DPS | AHU-1 FINE-FILTER DIFFERENTIAL PRESSURE HIGH
DPIT-5 | DIFFERENTIAL PRESSURE MAINTENANCE SUPERVISOR OFFICE | AHU1_AF_DPS | AHU-1 FAN AIR FLOW DIFFERENTIAL PRESSURE
DPIT-6 | DIFFERENTIAL PRESSURE TELECOM F&G ROOM | AHU2_PF_DPS | AHU-2 PRE-FILTER DIFFERENTIAL PRESSURE HIGH
DPIT-7 | DIFFERENTIAL PRESSURE TELECOM F&G ROOM AIRLOCK | AHU2_FF_DPS | AHU-2 FINE-FILTER DIFFERENTIAL PRESSURE HIGH
DPIT-8 | DIFFERENTIAL PRESSURE TEA ROOM | AHU2_AF_DPS | AHU-2 FAN AIR FLOW DIFFERENTIAL PRESSURE
DPIT-9 | DIFFERENTIAL PRESSURE TOILET | TOILET_FAN_DPS | DIFFERENTIAL PRESSURE ACROSS TOILET ROOM FAN-1&2
TT-001 | FRESH AIR DUCT TEMPERATURE
TT-002 | COMMON SUPPLY AIR DUCT TEMPERATURE
TT-003 | COMMON RETURN AIR DUCT TEMPERATURE
TT-004 | HVAC ROOM TEMPERATURE
TT-005 | EQUIPMENT TOOL ROOM TEMPERATURE
TT-006 | MACHINE WORKSHOP TEMPERATURE
TT-007 | E&I WORKSHOP TEMPERATURE
TT-008 | CONSUMABLE STORE TEMPERATURE
TT-009 | EU OPERATORS OFFICE TEMPERATURE
TT-010 | MAINTENANCE SUPERVISOR OFFICE TEMPERATURE
TT-011 | TEA ROOM TEMPERATURE
TT-012 | TOILET TEMPERATURE
HT-001 | COMMON RETURN AIR DUCT HUMIDITY
HT-002 | HVAC ROOM HUMIDITY
HT-003 | EQUIPMENT TOOL ROOM HUMIDITY
HT-004 | MACHINE WORKSHOP HUMIDITY
HT-005 | E&I WORKSHOP HUMIDITY
HT-006 | CONSUMABLE STORE HUMIDITY
HT-007 | EU OPERATORS OFFICE HUMIDITY
HT-008 | MAINTENANCE SUPERVISOR OFFICE HUMIDITY
HT-009 | TEA ROOM HUMIDITY
HT-010 | TOILET HUMIDITY
QTY | DESCRIPTION | QTY | DESCRIPTION
1 | DPIT - DUCT MOUNTED - OUTSIDE | 2 | FS - CHILLER SPPLY LINE MOUNTED - OUTSIDE
7 | DPIT - WALL MOUNTED - INSIDE THE ROOM | 4 | DPS - AHU OUTSIDE MOUNTED
1 | TT - DUCT MOUNTED - OUTSIDE | 2 | FS - INSIDE AHU MOUNTED
2 | TT -DUCT MOUNTED - INSIDE THE ROOM | 1 | DPS - TOILET ROOM
8 | TT - WALL MOUNTED - INSIDE THE ROOM
1 | HT -DUCT MOUNTED - INSIDE THE ROOM
8 | HT - WALL MOUNTED - INSIDE THE ROOM
1 | DPIT - WALL MOUNTED - INSIDE THE BAT.ROOM.EX
1 | TT - WALL MOUNTED - INSIDE THE BAT.ROOM.EX
1 | HT - WALL MOUNTED - INSIDE THE BAT.ROOM.EX