## DI
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
SUBSTATION-01
RUWAIS - U.A.E.
[10 empty] | FACILITY NAME: BOROUGE 4 |  |  |  | COMPANY PROJ. NO. |  | 4700000897
[14 empty] | CONTRACTOR. PROJ. NO. |  | 083118C
|  | SS-01-HVAC-CP | [7 empty] | DOCUMENT TITLE: OS HVAC PLC System - I/O List REV 2 |  |  |  | SUBCONTR. ID |  | -
Sl. No. | IM Module | I/O Detail |  |  |  |  | FROM | EQUIPMENT TAG | PLC TAG | Description | States |  | PLC Term. | TB GROUP |  | Verified & Signed (Remarks)
|  | Module | Supply | Type | Range | Unit |  |  |  |  | FALSE | TRUE
DIGITAL INPUT
1 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 141-GC-0103A | CHLR1_RUN | CHILLER-1 UNIT RUN STATUS | STOPPED | RUNNING | I0.0 | XDI1-1 | XDI1-2
2 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 141-GC-0103A | CHLR1_TRP | CHILLER-1 UNIT TRIP STATUS | NORMAL | TRIP | I0.1 | XDI1-3 | XDI1-4
3 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 141-GC-0103A | CHLR1_RMT | CHILLER-1 REMOTE MODE STATUS | LOCAL | REMOTE | I0.2 | XDI1-5 | XDI1-6
4 | IM1 | DI1 | 24VDC | VF | - | - | MCC | 141-GC-0103A | CHLR1_BRK_TRP | CHILLER-1 UNIT BREAKER TRIP STATUS | NORMAL | TRIP | I0.3 | XDI1-7 | XDI1-8
5 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 141-GC-0103B | CHLR2_RUN | CHILLER-2 UNIT RUN STATUS | STOPPED | RUNNING | I0.4 | XDI1-9 | XDI1-10
6 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 141-GC-0103B | CHLR2_TRP | CHILLER-2 UNIT TRIP STATUS | NORMAL | TRIP | I0.5 | XDI1-11 | XDI1-12
7 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 141-GC-0103B | CHLR2_RMT | CHILLER-2 REMOTE MODE STATUS | LOCAL | REMOTE | I0.6 | XDI1-13 | XDI1-14
8 | IM1 | DI1 | 24VDC | VF | - | - | MCC | 141-GC-0103B | CHLR2_BRK_TRP | CHILLER-2 UNIT BREAKER TRIP STATUS | NORMAL | TRIP | I0.7 | XDI1-15 | XDI1-16
9 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 141-GA-0103A | AHU1_RUN | AHU-1 RUN STATUS | STOPPED | RUNNING | I1.4 | XDI1-17 | XDI1-18
10 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 141-GA-0103A | AHU1_TRP | AHU-1 TRIP STATUS | NORMAL | TRIP | I1.5 | XDI1-19 | XDI1-20
11 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 141-GA-0103A | AHU1_RMT | AHU-1 REMOTE MODE STATUS | LOCAL | REMOTE | I1.6 | XDI1-21 | XDI1-22
12 | IM1 | DI1 | 24VDC | VF | - | - | MCC | 141-GA-0103A | AHU1_BRK_TRP | AHU-1 UNIT BREAKER TRIP STATUS | NORMAL | TRIP | I1.7 | XDI1-23 | XDI1-24
13 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 141-GA-0103A | AHU1_PF_DPS | AHU-1 PRE-FILTER DIFFERENTIAL PRESSURE HIGH | NORMAL | ALARM | I2.0 | XDI1-25 | XDI1-26
14 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 141-GA-0103A | AHU1_FF_DPS | AHU-1 FINE-FILTER DIFFERENTIAL PRESSURE HIGH | NORMAL | ALARM | I2.1 | XDI1-27 | XDI1-28
15 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 141-GA-0103A | AHU1_AF_DPS | AHU-1 FAN AIR FLOW DIFFERENTIAL PRESSURE | NO FLOW | FLOW ON | I2.2 | XDI1-29 | XDI1-30
16 | IM1 | DI1 | 24VDC | VF | - | - | FIELD | 141-GA-0103B | AHU2_RUN | AHU-2 RUN STATUS | STOPPED | RUNNING | I3.1 | XDI1-31 | XDI1-32
17 | IM1 | DI2 | 24VDC | VF | - | - | FIELD | 141-GA-0103B | AHU2_TRP | AHU-2 TRIP STATUS | NORMAL | TRIP | I3.2 | XDI2-1 | XDI2-2
18 | IM1 | DI2 | 24VDC | VF | - | - | FIELD | 141-GA-0103B | AHU2_RMT | AHU-2 REMOTE MODE STATUS | LOCAL | REMOTE | I3.3 | XDI2-3 | XDI2-4
19 | IM1 | DI2 | 24VDC | VF | - | - | MCC | 141-GA-0103B | AHU2_BRK_TRP | AHU-2 UNIT BREAKER TRIP STATUS | NORMAL | TRIP | I3.4 | XDI2-5 | XDI2-6
20 | IM1 | DI2 | 24VDC | VF | - | - | FIELD | 141-GA-0103B | AHU2_PF_DPS | AHU-2 PRE-FILTER DIFFERENTIAL PRESSURE HIGH | NORMAL | ALARM | I3.5 | XDI2-7 | XDI2-8
21 | IM1 | DI2 | 24VDC | VF | - | - | FIELD | 141-GA-0103B | AHU2_FF_DPS | AHU-2 FINE-FILTER DIFFERENTIAL PRESSURE HIGH | NORMAL | ALARM | I3.6 | XDI2-9 | XDI2-10
22 | IM1 | DI2 | 24VDC | VF | - | - | FIELD | 141-GA-0103B | AHU2_AF_DPS | AHU-2 FAN AIR FLOW DIFFERENTIAL PRESSURE | NO FLOW | FLOW ON | I3.7 | XDI2-11 | XDI2-12
23 | IM1 | DI2 | 24VDC | VF | - | - | MCC | 141-GK-0102A | BAT_FAN1_RUN | BATTERY ROOM FAN-1 RUN STATUS | STOPPED | RUNNING | I6.3 | XDI2-13 | XDI2-14
24 | IM1 | DI2 | 24VDC | VF | - | - | MCC | 141-GK-0102A | BAT_FAN1_TRP | BATTERY ROOM FAN-1 TRIP STATUS | NORMAL | TRIP | I6.4 | XDI2-15 | XDI2-16
25 | IM1 | DI2 | 24VDC | VF | - | - | MCC | 141-GK-0102A | BAT_FAN1_RMT | BATTERY ROOM FAN-1 REMOTE MODE STATUS | LOCAL | REMOTE | I6.5 | XDI2-17 | XDI2-18
26 | IM1 | DI2 | 24VDC | VF | - | - | MCC | 141-GK-0102A | BAT_FAN1_ES | BATTERY ROOM FAN-1 EMERGENCY STOP | NORMAL | ACTIVE | I6.6 | XDI2-19 | XDI2-20
27 | IM1 | DI2 | 24VDC | VF | - | - | MCC | 141-GK-0102B | BAT_FAN2_RUN | BATTERY ROOM FAN-2 RUN STATUS | STOPPED | RUNNING | I6.7 | XDI2-21 | XDI2-22
28 | IM1 | DI2 | 24VDC | VF | - | - | MCC | 141-GK-0102B | BAT_FAN2_TRP | BATTERY ROOM FAN-2 TRIP STATUS | NORMAL | TRIP | I7.0 | XDI2-23 | XDI2-24
29 | IM1 | DI2 | 24VDC | VF | - | - | MCC | 141-GK-0102B | BAT_FAN2_RMT | BATTERY ROOM FAN-2 REMOTE MODE STATUS | LOCAL | REMOTE | I7.1 | XDI2-25 | XDI2-26
30 | IM1 | DI2 | 24VDC | VF | - | - | MCC | 141-GK-0102B | BAT_FAN2_ES | BATTERY ROOM FAN-2 EMERGENCY STOP | NORMAL | ACTIVE | I7.2 | XDI2-27 | XDI2-28
31 | IM1 | DI2 | 24VDC | VF | - | - | MCC | 141-GK-0110 | BLD_FAN_RUN | BLEED FAN RUN STATUS | STOPPED | RUNNING | I6.3 | XDI2-29 | XDI2-30
32 | IM1 | DI2 | 24VDC | VF | - | - | MCC | 141-GK-0110 | BLD_FAN_TRP | BLEED FAN TRIP STATUS | NORMAL | TRIP | I6.4 | XDI2-31 | XDI2-32
33 | IM1 | DI3 | 24VDC | VF | - | - | MCC | 141-GK-0110 | BLD_FAN_RMT | BLEED FAN REMOTE MODE STATUS | LOCAL | REMOTE | I6.5 | XDI3-1 | XDI3-2
34 | IM1 | DI3 | 24VDC | VF | - | - | MCC | 141-GK-0110 | BLD_FAN_ES | BLEED FAN EMERGENCY STOP | NORMAL | ACTIVE | I6.6 | XDI3-3 | XDI3-4
35 | IM1 | DI3 | 24VDC | VF | - | - | MCC | 141-PC-0103A | CHLR1_PMP_RUN | CHILLER-1 WATER PUMP RUN STATUS | STOPPED | RUNNING | I6.3 | XDI3-5 | XDI3-6
36 | IM1 | DI3 | 24VDC | VF | - | - | MCC | 141-PC-0103A | CHLR1_PMP_TRP | CHILLER-1 WATER PUMP TRIP STATUS | NORMAL | TRIP | I6.4 | XDI3-7 | XDI3-8
37 | IM1 | DI3 | 24VDC | VF | - | - | MCC | 141-PC-0103A | CHLR1_PMP_RMT | CHILLER-1 WATER PUMP REMOTE MODE STATUS | LOCAL | REMOTE | I6.5 | XDI3-9 | XDI3-10
38 | IM1 | DI3 | 24VDC | VF | - | - | MCC | 141-PC-0103A | CHLR1_PMP_ES | CHILLER-1 WATER PUMP EMERGENCY STOP | NORMAL | ACTIVE | I6.6 | XDI3-11 | XDI3-12
39 | IM1 | DI3 | 24VDC | VF | - | - | MCC | 141-PC-0103B | CHLR2_PMP_RUN | CHILLER-2 WATER PUMP RUN STATUS | STOPPED | RUNNING | I6.3 | XDI3-13 | XDI3-14
40 | IM1 | DI3 | 24VDC | VF | - | - | MCC | 141-PC-0103B | CHLR2_PMP_TRP | CHILLER-2 WATER PUMP TRIP STATUS | NORMAL | TRIP | I6.4 | XDI3-15 | XDI3-16
41 | IM1 | DI3 | 24VDC | VF | - | - | MCC | 141-PC-0103B | CHLR2_PMP_RMT | CHILLER-2 WATER PUMP REMOTE MODE STATUS | LOCAL | REMOTE | I6.5 | XDI3-17 | XDI3-18
42 | IM1 | DI3 | 24VDC | VF | - | - | MCC | 141-PC-0103B | CHLR2_PMP_ES | CHILLER-2 WATER PUMP EMERGENCY STOP | NORMAL | ACTIVE | I6.6 | XDI3-19 | XDI3-20
43 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0103 | 141-MFD-0103-ZIO | MOTORIZED FIRE DAMPER 141-GD-0103 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI3-21 | XDI3-22
44 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0103 | 141-MFD-0103-ZIC | MOTORIZED FIRE DAMPER 141-GD-0103 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI3-23 | XDI3-24
45 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0104 | 141-MFD-0104-ZIO | MOTORIZED FIRE DAMPER 141-GD-0104 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI3-25 | XDI3-26
46 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0104 | 141-MFD-0104-ZIC | MOTORIZED FIRE DAMPER 141-GD-0104 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI3-27 | XDI3-28
47 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0107 | 141-MFD-0107-ZIO | MOTORIZED FIRE DAMPER 141-GD-0107 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI3-29 | XDI3-30
48 | IM1 | DI3 | 24VDC | VF | - | - | FIELD | 141-GD-0107 | 141-MFD-0107-ZIC | MOTORIZED FIRE DAMPER 141-GD-0107 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI3-31 | XDI3-32
49 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0108 | 141-MFD-0108-ZIO | MOTORIZED FIRE DAMPER 141-GD-0108 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI4-1 | XDI4-2
50 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0108 | 141-MFD-0108-ZIC | MOTORIZED FIRE DAMPER 141-GD-0108 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI4-3 | XDI4-4
51 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0109 | 141-MFD-0109-ZIO | MOTORIZED FIRE DAMPER 141-GD-0109 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI4-5 | XDI4-6
52 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0109 | 141-MFD-0109-ZIC | MOTORIZED FIRE DAMPER 141-GD-0109 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI4-7 | XDI4-8
53 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0110 | 141-MFD-0110-ZIO | MOTORIZED FIRE DAMPER 141-GD-0110 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI4-9 | XDI4-10
54 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0110 | 141-MFD-0110-ZIC | MOTORIZED FIRE DAMPER 141-GD-0110 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI4-11 | XDI4-12
55 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0112 | 141-MFD-0112-ZIO | MOTORIZED FIRE DAMPER 141-GD-0112 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI4-13 | XDI4-14
56 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0112 | 141-MFD-0112-ZIC | MOTORIZED FIRE DAMPER 141-GD-0112 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI4-15 | XDI4-16
57 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0113 | 141-MFD-0113-ZIO | MOTORIZED FIRE DAMPER 141-GD-0113 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI4-17 | XDI4-18
58 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0113 | 141-MFD-0113-ZIC | MOTORIZED FIRE DAMPER 141-GD-0113 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI4-19 | XDI4-20
59 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0116 | 141-MFD-0116-ZIO | MOTORIZED FIRE DAMPER 141-GD-0116 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI4-21 | XDI4-22
60 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0116 | 141-MFD-0116-ZIC | MOTORIZED FIRE DAMPER 141-GD-0116 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI4-23 | XDI4-24
61 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0117 | 141-MFD-0117-ZIO | MOTORIZED FIRE DAMPER 141-GD-0117 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI4-25 | XDI4-26
62 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0117 | 141-MFD-0117-ZIC | MOTORIZED FIRE DAMPER 141-GD-0117 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI4-27 | XDI4-28
63 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0118 | 141-MFD-0118-ZIO | MOTORIZED FIRE DAMPER 141-GD-0118 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI4-29 | XDI4-30
64 | IM1 | DI4 | 24VDC | VF | - | - | FIELD | 141-GD-0118 | 141-MFD-0118-ZIC | MOTORIZED FIRE DAMPER 141-GD-0118 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI4-31 | XDI4-32
65 | IM1 | DI5 | 24VDC | VF | - | - | FIELD | 141-GD-0119 | 141-MFD-0119-ZIO | MOTORIZED FIRE DAMPER 141-GD-0119 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI5-1 | XDI5-2
66 | IM1 | DI5 | 24VDC | VF | - | - | FIELD | 141-GD-0119 | 141-MFD-0119-ZIC | MOTORIZED FIRE DAMPER 141-GD-0119 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI5-3 | XDI5-4
67 | IM1 | DI5 | 24VDC | VF | - | - | FIELD | 141-GD-0120 | 141-MFD-0120-ZIO | MOTORIZED FIRE DAMPER 141-GD-0120 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI5-5 | XDI5-6
68 | IM1 | DI5 | 24VDC | VF | - | - | FIELD | 141-GD-0120 | 141-MFD-0120-ZIC | MOTORIZED FIRE DAMPER 141-GD-0120 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI5-7 | XDI5-8
69 | IM1 | DI5 | 24VDC | VF | - | - | FIELD | 141-GD-0121 | 141-MFD-0121-ZIO | MOTORIZED FIRE DAMPER 141-GD-0121 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI5-9 | XDI5-10
70 | IM1 | DI5 | 24VDC | VF | - | - | FIELD | 141-GD-0121 | 141-MFD-0121-ZIC | MOTORIZED FIRE DAMPER 141-GD-0121 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI5-11 | XDI5-12
71 | IM1 | DI5 | 24VDC | VF | - | - | FIELD | 141-GD-0122 | 141-MFD-0122-ZIO | MOTORIZED FIRE DAMPER 141-GD-0122 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI5-13 | XDI5-14
72 | IM1 | DI5 | 24VDC | VF | - | - | FIELD | 141-GD-0122 | 141-MFD-0122-ZIC | MOTORIZED FIRE DAMPER 141-GD-0122 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI5-15 | XDI5-16
73 | IM1 | DI5 | 24VDC | VF | - | - | FIELD | 141-GD-0123 | 141-MFD-0123-ZIO | MOTORIZED FIRE DAMPER 141-GD-0123 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI5-17 | XDI5-18
74 | IM1 | DI5 | 24VDC | VF | - | - | FIELD | 141-GD-0123 | 141-MFD-0123-ZIC | MOTORIZED FIRE DAMPER 141-GD-0123 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI5-19 | XDI5-20
75 | IM1 | DI5 | 24VDC | VF | - | - | FIELD | 141-GD-0124 | 141-MFD-0124-ZIO | MOTORIZED FIRE DAMPER 141-GD-0124 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI5-21 | XDI5-22
76 | IM1 | DI5 | 24VDC | VF | - | - | FIELD | 141-GD-0124 | 141-MFD-0124-ZIC | MOTORIZED FIRE DAMPER 141-GD-0124 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI5-23 | XDI5-24
77 | IM1 | DI5 | 24VDC | VF | - | - | FIELD | 141-GD-0125 | 141-MFD-0125-ZIO | MOTORIZED FIRE DAMPER 141-GD-0125 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI5-25 | XDI5-26
78 | IM1 | DI5 | 24VDC | VF | - | - | FIELD | 141-GD-0125 | 141-MFD-0125-ZIC | MOTORIZED FIRE DAMPER 141-GD-0125 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI5-27 | XDI5-28
79 | IM1 | DI5 | 24VDC | VF | - | - | FIELD | 141-GD-0126 | 141-MFD-0126-ZIO | MOTORIZED FIRE DAMPER 141-GD-0126 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI5-29 | XDI5-30
80 | IM1 | DI5 | 24VDC | VF | - | - | FIELD | 141-GD-0126 | 141-MFD-0126-ZIC | MOTORIZED FIRE DAMPER 141-GD-0126 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI5-31 | XDI5-32
81 | IM1 | DI6 | 24VDC | VF | - | - | FIELD | 141-GD-0127 | 141-MFD-0127-ZIO | MOTORIZED FIRE DAMPER 141-GD-0127 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI6-1 | XDI6-2
82 | IM1 | DI6 | 24VDC | VF | - | - | FIELD | 141-GD-0127 | 141-MFD-0127-ZIC | MOTORIZED FIRE DAMPER 141-GD-0127 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI6-3 | XDI6-4
83 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | CHLR1-BFV-ZIO | MOTORIZED BUTTER FLY VALVE CHILLER-1 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI6-5 | XDI6-6
84 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | CHLR1-BFV-ZIC | MOTORIZED BUTTER FLY VALVE CHILLER-1 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI6-7 | XDI6-8
85 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | CHLR2-BFV-ZIO | MOTORIZED BUTTER FLY VALVE CHILLER-2 OPEN STATUS | NOT OPEN | OPEN | I9.6 | XDI6-9 | XDI6-10
86 | IM1 | DI6 | 24VDC | VF | - | - | FIELD |  | CHLR2-BFV-ZIC | MOTORIZED BUTTER FLY VALVE CHILLER-2 CLOSE STATUS | NOT CLOSE | CLOSE | I9.7 | XDI6-11 | XDI6-12
87 | IM1 | DI6 | 24VDC | VF | - | - | FIELD | 141-GK-0102A | BAT_FAN1_DPS | DIFFERENTIAL PRESSURE ACROSS BATTERY ROOM FAN-1 | NO FLOW | FLOW ON | I9.6 | XDI6-13 | XDI6-14
88 | IM1 | DI6 | 24VDC | VF | - | - | FIELD | 141-GK-0102B | BAT_FAN2_DPS | DIFFERENTIAL PRESSURE ACROSS BATTERY ROOM FAN-2 | NO FLOW | FLOW ON | I9.7 | XDI6-15 | XDI6-16
89 | IM1 | DI6 | 24VDC | VF | - | - | FIELD | 141-GB-0112 | SWG_HTR_TRP | LV SWITCHGEAR ROOM HEATER-1 TRIP STATUS | NORMAL | TRIP | I9.6 | XDI6-17 | XDI6-18
90 | IM1 | DI6 | 24VDC | VF | - | - | FIELD | 141-GB-0107 | SWG_HTR_TRP | LV SWITCHGEAR ROOM HEATER-2 TRIP STATUS | NORMAL | TRIP | I9.7 | XDI6-19 | XDI6-20
91 | IM1 | DI6 | 24VDC | VF | - | - | FIELD | 141-GB-0106 | SWG_HTR_TRP | HV SWITCHGEAR ROOM HEATER TRIP STATUS | NORMAL | TRIP | I9.6 | XDI6-21 | XDI6-22
92 | IM1 | DI6 | 24VDC | VF | - | - | FIELD | 141-GB-0108 | RR_HTR_TRP | RACK ROOM HEATER TRIP STATUS | NORMAL | TRIP | I9.7 | XDI6-23 | XDI6-24
93 | IM1 | DI6 | 24VDC | VF | - | - | FIELD | 141-GB-0110 | BAT_HTR_TRP | BATTERY ROOM HEATER TRIP STATUS | NORMAL | TRIP | I9.6 | XDI6-25 | XDI6-26
94 | IM1 | DI6 | 24VDC | VF | - | - | FIELD | 141-GB-0111 | UPS_HTR_TRP | UPS ROOM HEATER TRIP STATUS | NORMAL | TRIP | I9.7 | XDI6-27 | XDI6-28
95 | IM1 | DI6 | 24VDC | VF | - | - | FIELD | 141-GB-0109 | TLR_HTR_TRP | TELECOM ROOM HEATER TRIP STATUS | NORMAL | TRIP | I9.6 | XDI6-29 | XDI6-30
96 | IM1 | DI6 | 24VDC | VF | - | - | FIELD | 141-GB-0112 | SWG_HTR_xxx | LV SWITCHGEAR ROOM HEATER-1 ON/OFF STATUS | NORMAL | TRIP | I9.7 | XDI6-31 | XDI6-32
97 | IM1 | DI7 | 24VDC | VF | - | - | FIELD | 141-GB-0107 | SWG_HTR_xxx | LV SWITCHGEAR ROOM HEATER-2 ON/OFF STATUS | NORMAL | TRIP | I9.6 | XDI7-1 | XDI7-2
98 | IM1 | DI7 | 24VDC | VF | - | - | FIELD | 141-GB-0106 | SWG_HTR_xxx | HV SWITCHGEAR ROOM HEATER ON/OFF STATUS | NORMAL | TRIP | I9.7 | XDI7-3 | XDI7-4
99 | IM1 | DI7 | 24VDC | VF | - | - | FIELD | 141-GB-0108 | RR_HTR_xxx | RACK ROOM HEATER ON/OFF STATUS | NORMAL | TRIP | I9.6 | XDI7-5 | XDI7-6
100 | IM1 | DI7 | 24VDC | VF | - | - | FIELD | 141-GB-0110 | BAT_HTR_xxx | BATTERY ROOM HEATER ON/OFF STATUS | NORMAL | TRIP | I9.7 | XDI7-7 | XDI7-8
101 | IM1 | DI7 | 24VDC | VF | - | - | FIELD | 141-GB-0111 | UPS_HTR_xxx | UPS ROOM HEATER ON/OFF STATUS | NORMAL | TRIP | I11.6 | XDI7-9 | XDI7-10
102 | IM1 | DI7 | 24VDC | VF | - | - | FIELD | 141-GB-0109 | TLR_HTR_xxx | TELECOM ROOM HEATER ON/OFF STATUS | NORMAL | TRIP | I11.7 | XDI7-11 | XDI7-12
103 | IM1 | DI7 | 24VDC | VF | - | - | PLC PANEL | - | EMG_STP | HVACP EMERGENCY STOP | NORMAL | ACTIVE | I12.2 | XDI7-13 | XDI7-14
104 | IM1 | DI7 | 24VDC | VF | - | - | PLC PANEL | - | MUTE_PB | MUTE PUSH BUTTON | OFF | ON | I12.2 | XDI7-15 | XDI7-16
105 | IM1 | DI7 | 24VDC | VF | - | - | PLC PANEL | - | RST_PB | RESET PUSH BUTTON | OFF | ON | I12.2 | XDI7-17 | XDI7-18
106 | IM1 | DI7 | 24VDC | VF | - | - | PLC PANEL | - | PSU1&2_HLTHY | POWER SUPPLY 1 & 2 HEALTHY | UNHEALTHY | HEALTHY | I12.2 | XDI7-19 | XDI7-20
107 | IM1 | DI7 | 24VDC | VF | - | - | PLC PANEL | - | AFS_HLTHY | PANEL AIR FLOW SWITCH HEALTHY | UNHEALTHY | HEALTHY | I12.3 | XDI7-21 | XDI7-22
108 | IM1 | DI7 | 24VDC | VF | - | - | PWR PANEL | - | EMG_MODE | EMERGENCY MODE | EMG MODE OFF | EMG MODE ON | I12.4 | XDI7-23 | XDI7-24
109 | IM1 | DI7 | 24VDC | VF | - | - | LFCP |  | HVAC_SHUT | HVAC SHUTDOWN COMMAND FROM F&G | NORMAL | SHUTDOWN | I12.4 | XDI7-25 | XDI7-26
110 | IM1 | DI7 | 24VDC | VF | - | - | LFCP |  | HVAC_RECR | HVAC RECIRCULATION MODE FROM F&G | NORMAL | RECIRCUL | I12.2 | XDI7-27 | XDI7-28
111 | IM1 | DI7 | 24VDC | VF | - | - | LFCP |  | LFCP_ZONE1 | LFCP ZONE 1 SELECTION | NORMAL | RECIRCUL | I12.2 | XDI7-29 | XDI7-30
112 | IM1 | DI7 | 24VDC | VF | - | - | LFCP | - | LFCP_ZONE2 | LFCP ZONE 2 SELECTION | NOT SELECTED | SELECTED | I12.2 | XDI7-31 | XDI7-32
113 | IM1 | DI8 | 24VDC | VF | - | - | LFCP | - | LFCP_ZONE3 | LFCP ZONE 3 SELECTION | NOT SELECTED | SELECTED | I12.2 | XDI8-1 | XDI8-2
114 | IM1 | DI8 | 24VDC | VF | - | - | LFCP | - | LFCP_ZONE4 | LFCP ZONE 4 SELECTION | NOT SELECTED | SELECTED | I12.2 | XDI8-3 | XDI8-4
115 | IM1 | DI8 | 24VDC | VF | - | - | LFCP | - | LFCP_ZONE5 | LFCP ZONE 5 SELECTION | NOT SELECTED | SELECTED | I12.2 | XDI8-5 | XDI8-6
116 | IM1 | DI8 | 24VDC | VF | - | - | LFCP | - | LFCP_ZONE6 | LFCP ZONE 6 SELECTION | NOT SELECTED | SELECTED | I12.2 | XDI8-7 | XDI8-8
117 | IM1 | DI8 | 24VDC | VF | - | - | LFCP | - | LFCP_ZONE7 | LFCP ZONE 7 SELECTION | NOT SELECTED | SELECTED | I13.1 | XDI8-9 | XDI8-10
118 | IM1 | DI8 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | I13.2 | XDI8-11 | XDI8-12
119 | IM1 | DI8 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | I13.4 | XDI8-13 | XDI8-14
120 | IM1 | DI8 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | I13.5 | XDI8-15 | XDI8-16
121 | IM1 | DI8 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | I13.6 | XDI8-17 | XDI8-18
122 | IM1 | DI8 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | I13.7 | XDI8-19 | XDI8-20
123 | IM1 | DI8 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | I14.0 | XDI8-21 | XDI8-22
124 | IM1 | DI8 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | I14.1 | XDI8-23 | XDI8-24
125 | IM1 | DI8 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | I14.2 | XDI8-25 | XDI8-26
126 | IM1 | DI8 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | I14.3 | XDI8-27 | XDI8-28
127 | IM1 | DI8 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | I14.4 | XDI8-29 | XDI8-30
128 | IM1 | DI8 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | I14.5 | XDI8-31 | XDI8-32
129 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | I14.6 | XDI9-1 | XDI9-2
130 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | I14.7 | XDI9-3 | XDI9-4
131 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | I15.0 | XDI9-5 | XDI9-6
132 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | I15.1 | XDI9-7 | XDI9-8
133 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | I15.2 | XDI9-9 | XDI9-10
134 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | I15.3 | XDI9-11 | XDI9-12
135 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | I15.4 | XDI9-13 | XDI9-14
136 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | I15.5 | XDI9-15 | XDI9-16
137 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | I15.6 | XDI9-17 | XDI9-18
138 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | I15.7 | XDI9-19 | XDI9-20
139 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | I16.0 | XDI9-21 | XDI9-22
140 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | I16.1 | XDI9-23 | XDI9-24
141 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | I16.2 | XDI9-25 | XDI9-26
142 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | I16.3 | XDI9-27 | XDI9-28
143 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | I16.4 | XDI9-29 | XDI9-30
144 | IM1 | DI9 | 24VDC | VF | - | - | - | - | - | SPARE |  |  | I16.5 | XDI9-31 | XDI9-32

## DO
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
SUBSTATION-01
RUWAIS - U.A.E.
[10 empty] | FACILITY NAME: BOROUGE 4 |  |  |  | COMPANY PROJ. NO. |  | 4700000897
[14 empty] | CONTRACTOR. PROJ. NO. |  | 083118C
|  | SS-01-HVAC-CP | [7 empty] | DOCUMENT TITLE: OS HVAC PLC System - I/O List REV 2 |  |  |  | SUBCONTR. ID |  | -
Sl. No. | IM Module | I/O Detail |  |  |  |  | TO | EQUIPMENT TAG | PLC TAG | Description | STATES |  | PLC Term. | TB GROUP |  | Verified & Signed
|  | Module | Supply | Type | Range | Unit |  |  |  |  | FALSE | TRUE
DIGITAL OUTPUT
1 | IM1 | DO1 | 24VDC | VF | - | - | MCC | 141-GC-0103A | CHLR1_CMD | CHILLER-1 START/STOP COMMAND | STOP | START | Q0.0 | XDO1-1 | XDO1-2
2 | IM1 | DO1 | 24VDC | VF | - | - | MCC | 141-GC-0103B | CHLR2_CMD | CHILLER-2 START/STOP COMMAND | STOP | START | Q0.1 | XDO1-3 | XDO1-4
3 | IM1 | DO1 | 24VDC | VF | - | - | MCC | 141-GA-0103A | AHU1_CMD | AHU-1 START/STOP COMMAND | STOP | START | Q0.3 | XDO1-5 | XDO1-6
4 | IM1 | DO1 | 24VDC | VF | - | - | MCC | 141-GA-0103B | AHU2_CMD | AHU-2 START/STOP COMMAND | STOP | START | Q0.4 | XDO1-7 | XDO1-8
5 | IM1 | DO1 | 24VDC | VF | - | - | MCC | 141-GK-0102A | BAT_FAN1_CMD | BATTERY ROOM EXHAUST FAN-1 START/STOP COMMAND | STOP | START | Q1.2 | XDO1-9 | XDO1-10
6 | IM1 | DO1 | 24VDC | VF | - | - | MCC | 141-GK-0102B | BAT_FAN2_CMD | BATTERY ROOM EXHAUST FAN-2 START/STOP COMMAND | STOP | START | Q1.2 | XDO1-11 | XDO1-12
7 | IM1 | DO1 | 24VDC | VF | - | - | MCC |  | CHLR1_BFV_OPN | CHILLER-1 MOTORIZED BUTTER FLY VALVE OPEN COMMAND | NOT OPEN | OPEN | Q1.2 | XDO1-13 | XDO1-14
8 | IM1 | DO1 | 24VDC | VF | - | - | MCC |  | CHLR1_BFV_CLS | CHILLER-1 MOTORIZED BUTTER FLY VALVE CLOSE COMMAND | NOT CLOSE | CLOSE | Q1.2 | XDO1-15 | XDO1-16
9 | IM1 | DO1 | 24VDC | VF | - | - | MCC |  | CHLR2_BFV_OPN | CHILLER-2 MOTORIZED BUTTER FLY VALVE OPEN COMMAND | NOT OPEN | OPEN | Q1.2 | XDO1-17 | XDO1-18
10 | IM1 | DO1 | 24VDC | VF | - | - | MCC |  | CHLR2_BFV_CLS | CHILLER-2 MOTORIZED BUTTER FLY VALVE CLOSE COMMAND | NOT CLOSE | CLOSE | Q1.2 | XDO1-19 | XDO1-20
11 | IM1 | DO1 | 24VDC | VF | - | - | MCC | 141-PC-0103A | CHLR1_PMP_CMD | CHILLER-1 WATER PUMP START/STOP COMMAND | STOP | START | Q1.2 | XDO1-21 | XDO1-22
12 | IM1 | DO1 | 24VDC | VF | - | - | MCC | 141-PC-0103B | CHLR2_PMP_CMD | CHILLER-2 WATER PUMP START/STOP COMMAND | STOP | START | Q1.2 | XDO1-23 | XDO1-24
13 | IM1 | DO1 | 24VDC | VF | - | - | MCC | 141-GB-0112 | SWG_HTR1_CMD | LV SWITCHGEAR ROOM HEATER-1 ON/OFF COMMAND | OFF | ON | Q1.4 | XDO1-25 | XDO1-26
14 | IM1 | DO1 | 24VDC | VF | - | - | MCC | 141-GB-0107 | SWG_HTR2_CMD | LV SWITCHGEAR ROOM HEATER-2 ON/OFF COMMAND | OFF | ON | Q1.4 | XDO1-27 | XDO1-28
15 | IM1 | DO1 | 24VDC | VF | - | - | MCC | 141-GB-0106 | SWG_HTR3_CMD | HV SWITCHGEAR ROOM HEATER-2 ON/OFF COMMAND | OFF | ON | Q1.4 | XDO1-29 | XDO1-30
16 | IM1 | DO1 | 24VDC | VF | - | - | MCC | 141-GB-0108 | RR_HTR_CMD | RACK ROOM HEATER ON/OFF COMMAND | OFF | ON | Q1.5 | XDO1-31 | XDO1-32
17 | IM1 | DO2 | 24VDC | VF | - | - | MCC | 141-GB-0110 | BAT_HTR_CMD | BATTERY ROOM HEATER ON/OFF COMMAND | OFF | ON | Q1.6 | XDO2-1 | XDO2-2
18 | IM1 | DO2 | 24VDC | VF | - | - | MCC | 141-GB-0111 | UPS_HTR_CMD | UPS ROOM HEATER ON/OFF COMMAND | OFF | ON | Q1.6 | XDO2-3 | XDO2-4
19 | IM1 | DO2 | 24VDC | VF | - | - | MCC | 141-GB-0109 | TLR_HTR_CMD | TELECOM ROOM HEATER ON/OFF COMMAND | OFF | ON | Q1.6 | XDO2-5 | XDO2-6
20 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-GD-0103 | 141-MFD-0103-CMD | MOTORIZED FIRE DAMPER 141-GD-0103 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-7 | XDO2-8
21 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-GD-0104 | 141-MFD-0104-CMD | MOTORIZED FIRE DAMPER 141-GD-0104 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-9 | XDO2-10
22 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-GD-0107 | 141-MFD-0107-CMD | MOTORIZED FIRE DAMPER 141-GD-0107 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-11 | XDO2-12
23 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-GD-0108 | 141-MFD-0108-CMD | MOTORIZED FIRE DAMPER 141-GD-0108 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-13 | XDO2-14
24 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-GD-0109 | 141-MFD-0109-CMD | MOTORIZED FIRE DAMPER 141-GD-0109 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-15 | XDO2-16
25 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-GD-0110 | 141-MFD-0110-CMD | MOTORIZED FIRE DAMPER 141-GD-0110 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-17 | XDO2-18
26 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-GD-0112 | 141-MFD-0112-CMD | MOTORIZED FIRE DAMPER 141-GD-0112 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-19 | XDO2-20
27 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-GD-0113 | 141-MFD-0113-CMD | MOTORIZED FIRE DAMPER 141-GD-0113 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-21 | XDO2-22
28 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-GD-0116 | 141-MFD-0116-CMD | MOTORIZED FIRE DAMPER 141-GD-0116 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-23 | XDO2-24
29 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-GD-0117 | 141-MFD-0117-CMD | MOTORIZED FIRE DAMPER 141-GD-0117 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-25 | XDO2-26
30 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-GD-0118 | 141-MFD-0118-CMD | MOTORIZED FIRE DAMPER 141-GD-0118 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-27 | XDO2-28
31 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-GD-0119 | 141-MFD-0119-CMD | MOTORIZED FIRE DAMPER 141-GD-0119 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-29 | XDO2-30
32 | IM1 | DO2 | 24VDC | 240V | - | - | FIELD | 141-GD-0120 | 141-MFD-0120-CMD | MOTORIZED FIRE DAMPER 141-GD-0120 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO2-31 | XDO2-32
33 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-GD-0121 | 141-MFD-0121-CMD | MOTORIZED FIRE DAMPER 141-GD-0121 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-1 | XDO3-2
34 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-GD-0122 | 141-MFD-0122-CMD | MOTORIZED FIRE DAMPER 141-GD-0122 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-3 | XDO3-4
35 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-GD-0123 | 141-MFD-0123-CMD | MOTORIZED FIRE DAMPER 141-GD-0123 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-5 | XDO3-6
36 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-GD-0124 | 141-MFD-0124-CMD | MOTORIZED FIRE DAMPER 141-GD-0124 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-7 | XDO3-8
37 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-GD-0125 | 141-MFD-0125-CMD | MOTORIZED FIRE DAMPER 141-GD-0125 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-9 | XDO3-10
38 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-GD-0126 | 141-MFD-0126-CMD | MOTORIZED FIRE DAMPER 141-GD-0126 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-11 | XDO3-12
39 | IM1 | DO3 | 24VDC | 240V | - | - | FIELD | 141-GD-0127 | 141-MFD-0127-CMD | MOTORIZED FIRE DAMPER 141-GD-0127 OPEN/CLOSE COMMAND | CLOSE | OPEN | Q3.1 | XDO3-13 | XDO3-14
40 | IM1 | DO3 | 24VDC | VF | - | - | PLC | - | BUZZ_ON | BUZZER ON COMMAND | OFF | ON | Q3.1 | XDO3-15 | XDO3-16
41 | IM1 | DO3 | 24VDC | VF | - | - | LFCP | - | HVAC_SHUT_FG | HVAC SHUTDOWN FEEDBACK TO LFCP | OFF | ON | Q3.1 | XDO3-17 | XDO3-18
42 | IM1 | DO3 | 24VDC | VF | - | - | LFCP | - | HVAC_SHUT_FG | RECIRCULATION FEEDBACK TO LFCP | OFF | ON | Q3.1 | XDO3-19 | XDO3-20
43 | IM1 | DO3 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q3.1 | XDO3-21 | XDO3-22
44 | IM1 | DO3 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q3.1 | XDO3-23 | XDO3-24
45 | IM1 | DO3 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q3.1 | XDO3-25 | XDO3-26
46 | IM1 | DO3 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q3.1 | XDO3-27 | XDO3-28
47 | IM1 | DO3 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q4.7 | XDO3-29 | XDO3-30
48 | IM1 | DO3 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q4.7 | XDO3-31 | XDO3-32
49 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q5.0 | XDO4-1 | XDO4-2
50 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q4.1 | XDO4-3 | XDO4-4
51 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q4.2 | XDO4-5 | XDO4-6
52 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q4.3 | XDO4-7 | XDO4-8
53 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q1.7 | XDO4-9 | XDO4-10
54 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q2.0 | XDO4-11 | XDO4-12
55 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q2.1 | XDO4-13 | XDO4-14
56 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q2.2 | XDO4-15 | XDO4-16
57 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q2.3 | XDO4-17 | XDO4-18
58 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q2.4 | XDO4-19 | XDO4-20
59 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q2.5 | XDO4-21 | XDO4-22
60 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q2.6 | XDO4-23 | XDO4-24
61 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q2.7 | XDO4-25 | XDO4-26
62 | IM1 | DO4 | 24VDC | 24V | - | - | - | - | - | SPARE | - | - | Q3.0 | XDO4-27 | XDO4-28
63 | IM1 | DO4 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | Q5.1 | XDO4-29 | XDO4-30
64 | IM1 | DO4 | 24VDC | VF | - | - | - | - | - | SPARE | - | - | Q5.2 | XDO4-31 | XDO4-32

## AI
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
SUBSTATION-01
RUWAIS - U.A.E.
[10 empty] | FACILITY NAME: BOROUGE 4 | [5 empty] | COMPANY PROJ. NO. |  | 4700000897
[16 empty] | CONTRACTOR. PROJ. NO. |  | 083118C
| SS-01-HVAC-CP | [8 empty] | DOCUMENT TITLE: OS HVAC PLC System - I/O List REV 2 | [5 empty] | SUBCONTR. ID |  | -
Sl. No. | IM Module | I/O Detail |  |  |  |  | FROM | EQUIPMENT TAG | PLC TAG | Description | Alarm Setpoints |  |  |  | PLC Term. | TB GROUP |  | Verified & Signed
|  | Module | Supply | Type | Range | Unit |  |  |  |  | LL | L | H | HH
ANALOGUE INPUT
1 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-1 | DPIT-1 | DIFFERENTIAL PRESSURE HVAC ROOM | - | 1 | 5 | - | I0+/I0- | XAI1-1 | XAI1-2
2 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-2 | DPIT-2 | DIFFERENTIAL PRESSURE LV SWT. GR. ROOM | - | 1 | 5 | - | I1+/I1- | XAI1-3 | XAI1-4
3 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-3 | DPIT-3 | DIFFERENTIAL PRESSURE LV SWT. GR. AIRLOCK ROOM | - | 1 | 5 | - | I2+/I2- | XAI1-5 | XAI1-6
4 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-4 | DPIT-4 | DIFFERENTIAL PRESSURE HV SWT. GR. ROOM | - | 1 | 5 | - | I3+/I3- | XAI1-7 | XAI1-8
5 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-5 | DPIT-5 | DIFFERENTIAL PRESSURE RACK ROOM | - | 1 | 5 | - | I4+/I4- | XAI1-9 | XAI1-10
6 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-6 | DPIT-6 | DIFFERENTIAL PRESSURE RACK AIRLOCK ROOM | - | 1 | 5 | - | I5+/I5- | XAI1-11 | XAI1-12
7 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-7 | DPIT-7 | DIFFERENTIAL PRESSURE TELECOM ROOM | - | 1 | 5 | - | I6+/I6- | XAI1-13 | XAI1-14
8 | IM1 | AI1 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-8 | DPIT-8 | DIFFERENTIAL PRESSURE UPS ROOM | - | 1 | 5 | - | I7+/I7- | XAI1-15 | XAI1-16
9 | IM1 | AI2 | 24VDC | Sink | 0-6 | pa | FIELD | DPIT-9 | DPIT-9 | DIFFERENTIAL PRESSURE BATTERY ROOM | - | 1 | 5 | - | I0+/I0- | XAI2-1 | XAI2-2
10 | IM1 | AI2 | 24VDC | Sink | 0-55 | °C | FIELD | TT-001 | TT-001 | FRESH AIR DUCT TEMPERATURE | - | 20 | 30 | - | I1+/I1- | XAI2-3 | XAI2-4
11 | IM1 | AI2 | 24VDC | Sink | 0-55 | °C | FIELD | TT-002 | TT-002 | RACK ROOM SUPPLY AIR DUCT TEMPERATURE | - | 20 | 30 | - | I2+/I2- | XAI2-5 | XAI2-6
12 | IM1 | AI2 | 24VDC | Sink | 0-55 | °C | FIELD | TT-003 | TT-003 | LV SWT. GR. ROOM SUPPLY AIR DUCT TEMPERATURE | - | 20 | 30 | - | I3+/I3- | XAI2-7 | XAI2-8
13 | IM1 | AI2 | 24VDC | Sink | 0-55 | °C | FIELD | TT-004 | TT-004 | HVAC ROOM TEMPERATURE | - | 20 | 30 | - | I4+/I4- | XAI2-9 | XAI2-10
14 | IM1 | AI2 | 24VDC | Sink | 0-55 | °C | FIELD | TT-005 | TT-005 | LV SWT. GR. ROOM TEMPERATURE | - | 20 | 30 | - | I5+/I5- | XAI2-11 | XAI2-12
15 | IM1 | AI2 | 24VDC | Sink | 0-55 | °C | FIELD | TT-006 | TT-006 | HV SWT. GR. ROOM TEMPERATURE | - | 20 | 30 | - | I6+/I6- | XAI2-13 | XAI2-14
16 | IM1 | AI2 | 24VDC | Sink | 0-55 | °C | FIELD | TT-007 | TT-007 | RACK ROOM TEMPERATURE | - | 20 | 30 | - | I7+/I7- | XAI2-15 | XAI2-16
17 | IM1 | AI3 | 24VDC | Sink | 0-55 | °C | FIELD | TT-008 | TT-008 | TELECOM ROOM TEMPERATURE | - | 20 | 30 | - | I0+/I0- | XAI3-1 | XAI3-2
18 | IM1 | AI3 | 24VDC | Sink | 0-55 | °C | FIELD | TT-009 | TT-009 | UPS ROOM TEMPERATURE | - | 20 | 30 | - | I1+/I1- | XAI3-3 | XAI3-4
19 | IM1 | AI3 | 24VDC | Sink | 0-55 | °C | FIELD | TT-010 | TT-010 | BATTERY ROOM TEMPERATURE | - | 20 | 30 | - | I2+/I2- | XAI3-5 | XAI3-6
20 | IM1 | AI3 | 24VDC | Sink | 0-100 | °C | FIELD | HT-001 | HT-001 | RETURN AIR DUCT HUMIDITY | - | 30 | 60 | - | I3+/I3- | XAI3-7 | XAI3-8
21 | IM1 | AI3 | 24VDC | Sink | 0-101 | °C | FIELD | HT-002 | HT-002 | RACK ROOM RETURN AIR DUCT HUMIDITY | - | 30 | 60 | - | I4+/I4- | XAI3-9 | XAI3-10
22 | IM1 | AI3 | 24VDC | Sink | 0-102 | °C | FIELD | HT-003 | HT-003 | LV SWT. GR. ROOM RETURN AIR DUCT HUMIDITY | - | 30 | 60 | - | I5+/I5- | XAI3-11 | XAI3-12
23 | IM1 | AI3 | 24VDC | Sink | 0-103 | °C | FIELD | HT-004 | HT-004 | RACK ROOM SUPPLY AIR DUCT HUMIDITY | - | 30 | 60 | - | I6+/I6- | XAI3-13 | XAI3-14
24 | IM1 | AI3 | 24VDC | Sink | 0-104 | °C | FIELD | HT-005 | HT-005 | LV SWT. GR. ROOM SUPPLY AIR DUCT HUMIDITY | - | 30 | 60 | - | I7+/I7- | XAI3-15 | XAI3-16
25 | IM1 | AI4 | 24VDC | Sink | 0-55 | °C | FIELD | HT-006 | HT-006 | HVAC ROOM HUMIDITY | - | 30 | 60 | - | I0+/I0- | XAI4-1 | XAI4-2
26 | IM1 | AI4 | 24VDC | Sink | 0-55 | °C | FIELD | HT-007 | HT-007 | LV SWT. GR. ROOM HUMIDITY | - | 30 | 60 | - | I1+/I1- | XAI4-3 | XAI4-4
27 | IM1 | AI4 | 24VDC | Sink | 0-55 | °C | FIELD | HT-008 | HT-008 | HV SWT. GR. ROOM HUMIDITY | - | 30 | 60 | - | I2+/I2- | XAI4-5 | XAI4-6
28 | IM1 | AI4 | 24VDC | Sink | 0-55 | °C | FIELD | HT-009 | HT-009 | RACK ROOM HUMIDITY | - | 30 | 60 | - | I3+/I3- | XAI4-7 | XAI4-8
29 | IM1 | AI4 | 24VDC | Sink | 0-55 | °C | FIELD | HT-010 | HT-010 | TELECOM ROOM HUMIDITY | - | 30 | 60 | - | I4+/I4- | XAI4-9 | XAI4-10
30 | IM1 | AI4 | 24VDC | Sink | 0-55 | °C | FIELD | HT-011 | HT-011 | UPS ROOM HUMIDITY | - | 30 | 60 | - | I5+/I5- | XAI4-11 | XAI4-12
31 | IM1 | AI4 | 24VDC | Sink | 0-55 | °C | FIELD | HT-012 | HT-012 | BATTERY ROOM HUMIDITY | - | 30 | 60 | - | I6+/I6- | XAI4-13 | XAI4-14
32 | IM1 | AI4 | 24VDC | Sink | 0-1560 | rpm | FIELD | - | CHLR1-PMP-SPD-FB | CHILLER-1 WATER PUMP SPEED FEEDBACK | - | - | - | - | I7+/I7- | XAI4-15 | XAI4-16
33 | IM1 | AI5 | 24VDC | Sink | 0-100 | % | FIELD | 141-MD-0131 | 141-MD-0131-FB | MODULATING DAMPER MD-0131 POSITION FEEDBACK | - | - | - | - | I0+/I0- | XAI5-1 | XAI5-2
34 | IM1 | AI5 | 24VDC | Sink | 0-100 | % | FIELD | 141-MD-0132 | 141-MD-0132-FB | MODULATING DAMPER MD-0132 POSITION FEEDBACK | - | - | - | - | I1+/I1- | XAI5-3 | XAI5-4
35 | IM1 | AI5 | 24VDC | Sink | 0-100 | % | FIELD | 141-MD-0133 | 141-MD-0133-FB | MODULATING DAMPER MD-0133 POSITION FEEDBACK | - | - | - | - | I2+/I2- | XAI5-5 | XAI5-6
36 | IM1 | AI5 | 24VDC | Sink | 0-100 | % | FIELD | 141-MD-0134 | 141-MD-0134-FB | MODULATING DAMPER MD-0134 POSITION FEEDBACK | - | - | - | - | I3+/I3- | XAI5-7 | XAI5-8
37 | IM1 | AI5 | 24VDC | Sink | 0-100 | % | FIELD | 141-MD-0135 | 141-MD-0135-FB | MODULATING DAMPER MD-0135 POSITION FEEDBACK | - | - | - | - | I4+/I4- | XAI5-9 | XAI5-10
38 | IM1 | AI5 | 24VDC | Sink | 0-100 | % | FIELD | 141-MD-0136 | 141-MD-0136-FB | MODULATING DAMPER MD-0136 POSITION FEEDBACK | - | - | - | - | I5+/I5- | XAI5-11 | XAI5-12
39 | IM1 | AI5 | 24VDC | Sink | 0-100 | % | FIELD | 141-MD-0137 | 141-MD-0137-FB | MODULATING DAMPER MD-0137 POSITION FEEDBACK | - | - | - | - | I6+/I6- | XAI5-13 | XAI5-14
40 | IM1 | AI5 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I7+/I7- | XAI5-15 | XAI5-16
41 | IM1 | AI6 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I0+/I0- | XAI6-1 | XAI6-2
42 | IM1 | AI6 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I1+/I1- | XAI6-3 | XAI6-4
43 | IM1 | AI6 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I2+/I2- | XAI6-5 | XAI6-6
44 | IM1 | AI6 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I3+/I3- | XAI6-7 | XAI6-8
45 | IM1 | AI6 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I4+/I4- | XAI6-9 | XAI6-10
46 | IM1 | AI6 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I5+/I5- | XAI6-11 | XAI6-12
47 | IM1 | AI6 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I6+/I6- | XAI6-13 | XAI6-14
48 | IM1 | AI6 | 24VDC | Sink | - | - | FIELD | - | - | SPARE | - | - | - | - | I7+/I7- | XAI6-15 | XAI6-16

## AO
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
SUBSTATION-01
RUWAIS - U.A.E.
[10 empty] | FACILITY NAME: BOROUGE 4 | [5 empty] | COMPANY PROJ. NO. |  | 4700000897
[16 empty] | CONTRACTOR. PROJ. NO. |  | 083118C
| SS-01-HVAC-CP | [8 empty] | DOCUMENT TITLE: OS HVAC PLC System - I/O List REV 2 | [5 empty] | SUBCONTR. ID |  | -
Sl. No. | IM Module | I/O Detail |  |  |  |  | TO | EQUIPMENT TAG | PLC TAG | Description | Alarm Setpoints |  |  |  | PLC Term. | TB GROUP |  | Verified & Signed
|  | Module | Supply | Type | Range | Unit |  |  |  |  | LL | L | H | HH
ANALOGUE OUTPUT
1 | IM1 | AO1 | 24VDC | 4-20mA | - | - | CHILLER-1 | 141-GC-0103A | CHLR1_TMP_SP | TEMPERATURE SET POINT TO CHILLER-1 | - | - | - | - | Q0+/Q0- | XAO1-1 | XAO1-2
2 | IM1 | AO1 | 24VDC | 4-20mA | - | - | CHILLER-1 | 141-GC-0103A | CHLR1_RA_TMP | RETURN AIR TEMPETATURE TO CHILLER-1 | - | - | - | - | Q1+/Q1- | XAO1-3 | XAO1-4
3 | IM1 | AO1 | 24VDC | 4-20mA | - | - | CHILLER-2 | 141-GC-0103B | CHLR2_TMP_SP | TEMPERATURE SET POINT TO CHILLER-2 | - | - | - | - | Q2+/Q2- | XAO1-5 | XAO1-6
4 | IM1 | AO1 | 24VDC | 4-20mA | - | - | CHILLER-2 | 141-GC-0103B | CHLR2_RA_TMP | RETURN AIR TEMPETATURE TO CHILLER-2 | - | - | - | - | Q3+/Q3- | XAO1-7 | XAO1-8
5 | IM1 | AO2 | 24VDC | 4-20mA | - | - | - | - | CHLR1-PMP-SPD-REF | CHILLER-1 WATER PUMP SPEED SETPOINT | - | - | - | - | Q0+/Q0- | XAO2-1 | XAO2-2
6 | IM1 | AO2 | 24VDC | 4-20mA | - | - | - | 141-MD-0131 | 141-MD-0131-SP | MODULATING DAMPER MD-0131 SETPOINT | - | - | - | - | Q1+/Q1- | XAO2-3 | XAO2-4
7 | IM1 | AO2 | 24VDC | 4-20mA | - | - | - | 141-MD-0132 | 141-MD-0132-SP | MODULATING DAMPER MD-0132 SETPOINT | - | - | - | - | Q2+/Q2- | XAO2-5 | XAO2-6
8 | IM1 | AO2 | 24VDC | 4-20mA | - | - | - | 141-MD-0133 | 141-MD-0133-SP | MODULATING DAMPER MD-0133 SETPOINT | - | - | - | - | Q3+/Q3- | XAO2-7 | XAO2-8
9 | IM1 | AO3 | 24VDC | 4-20mA | - | - | - | 141-MD-0134 | 141-MD-0134-SP | MODULATING DAMPER MD-0134 SETPOINT | - | - | - | - | Q0+/Q0- | XAO3-1 | XAO3-2
10 | IM1 | AO3 | 24VDC | 4-20mA | - | - | - | 141-MD-0135 | 141-MD-0135-SP | MODULATING DAMPER MD-0135 SETPOINT | - | - | - | - | Q1+/Q1- | XAO3-3 | XAO3-4
11 | IM1 | AO3 | 24VDC | 4-20mA | - | - | - | 141-MD-0136 | 141-MD-0136-SP | MODULATING DAMPER MD-0136 SETPOINT | - | - | - | - | Q2+/Q2- | XAO3-5 | XAO3-6
12 | IM1 | AO3 | 24VDC | 4-20mA | - | - | - | 141-MD-0137 | 141-MD-0137-SP | MODULATING DAMPER MD-0137 SETPOINT | - | - | - | - | Q3+/Q3- | XAO3-7 | XAO3-8
13 | IM1 | AO4 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q0+/Q0- | XAO4-1 | XAO4-2
14 | IM1 | AO4 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q1+/Q1- | XAO4-3 | XAO4-4
15 | IM1 | AO4 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q2+/Q2- | XAO4-5 | XAO4-6
16 | IM1 | AO4 | 24VDC | 4-20mA | - | - | - | - | - | SPARE | - | - | - | - | Q3+/Q3- | XAO4-7 | XAO4-8

## IO Summary
PROJECT NAME: EP PACKAGE 2 (ETHANE CRACKER)
SUBSTATION-01
RUWAIS - U.A.E.
[8 empty] | FACILITY NAME: BOROUGE 4 | COMPANY PROJ. NO. | 4700000897
[9 empty] | CONTRACTOR. PROJ. NO. | 083118C
SS-01-HVAC-CP | [7 empty] | DOCUMENT TITLE: OS HVAC PLC System - I/O List REV 2 | SUBCONTR. ID | -
IO SUMMARY
Sl.No | Type | No. Of Channels | No. Of Modules | Count | Used | Spare | Spare %
1 | DI | 16 | 9 | 144 | 117 | 27 | 23.0769
2 | DO | 16 | 4 | 64 | 42 | 22 | 52.381
3 | AI | 8 | 6 | 48 | 39 | 9 | 23.0769
4 | AO | 4 | 4 | 16 | 12 | 4 | 33.3333